## Scalars
Parameter | Description (units) | Value | Type | Source | Source URL
usd_to_gbp | USD to GBP conversion rate [GBP/USD] | 0.75 | Standing assumption | Assumed planning rate (approx. 2024-2025 USD-GBP)
eur_to_gbp | EUR to GBP conversion rate [GBP/EUR] | 0.85 | Standing assumption | Assumed planning rate (approx. 2024-2025 EUR-GBP)
general_inflation | Real O&M cost escalation [/yr] | 0 | Standing assumption | Model is in real prices.
discount_rate | Real discount rate / WACC [/yr] | 0.035 | Verified assumption | HM Treasury Green Book (pp 40) | https://www.gov.uk/government/publications/the-green-book-appraisal-and-evaluation-in-central-government | https://www.gov.uk/government/publications/the-green-book-appraisal-and-evaluation-in-central-government
PRIMARY_ENERGY_FACTOR [electricity] | Primary energy factor, grid-supplied electricity [kWh primary / kWh delivered] | 1.501 | Verified assumption | NCM Modelling Guide for buildings other than dwellings in England, 2021 Edition (26 Sep 2022), Table 32 'Fuel CO2 emission and primary energy factors for district heat networks' (pp 60-61), rows 'Heat from electric heat pump' and 'Electricity for pumping in distribution network' = 1.501 kWhPE/kWh. | https://www.uk-ncm.org.uk/filelibrary/NCM_Modelling_Guide_2021_Edition_England_26Sep2022.pdf
PRIMARY_ENERGY_FACTOR [gas] | Primary energy factor, mains gas [kWh primary / kWh delivered] | 1.13 | Verified assumption | NCM Modelling Guide for buildings other than dwellings in England, 2021 Edition (26 Sep 2022), Table 32 'Fuel CO2 emission and primary energy factors for district heat networks' (pp 60-61), row 'Heat from boilers that use mains gas' = 1.13 kWhPE/kWh. | https://www.uk-ncm.org.uk/filelibrary/NCM_Modelling_Guide_2021_Edition_England_26Sep2022.pdf
GRID_IMPORT_LIMIT_KW [East Anglia] | DNO import (demand-headroom) connection ceiling - East Anglia [kW] | 7100 | Verified assumption | UKPN DFES NSHR (EPN): MEDIAN OF NON-ZERO headroom across primary substations (n=557, of which 1 at zero = 0%), present-day/2025 basis. Estimator changed from plain median: where a large share of primaries are fully saturated the plain median falls into the zero mass and describes the saturated tail rather than a typical connectable substation (plain median here = 7000 kW). Applied uniformly to all 9 districts for comparability. Reproducible via scripts/headroom_medians.py. | https://ukpowernetworks.opendatasoft.com/explore/dataset/dfes-network-headroom-report/
GRID_EXPORT_LIMIT_KW [East Anglia] | DNO export (generation-headroom) connection ceiling - East Anglia [kW] | 18260 | Verified assumption | UKPN DFES NSHR (EPN): MEDIAN OF NON-ZERO headroom across primary substations (n=553, of which 0 at zero = 0%), present-day/2025 basis. Estimator changed from plain median: where a large share of primaries are fully saturated the plain median falls into the zero mass and describes the saturated tail rather than a typical connectable substation (plain median here = 17710 kW). Applied uniformly to all 9 districts for comparability. Reproducible via scripts/headroom_medians.py. | https://ukpowernetworks.opendatasoft.com/explore/dataset/dfes-network-headroom-report/
GRID_IMPORT_LIMIT_KW [England E and NE] | DNO import (demand-headroom) connection ceiling - England E and NE [kW] | 10395 | Verified assumption | NPG Heat Map (NE+Yorkshire): MEDIAN OF NON-ZERO headroom across primary substations (n=508, of which 181 at zero = 36%), present-day/2025 basis. Estimator changed from plain median: where a large share of primaries are fully saturated the plain median falls into the zero mass and describes the saturated tail rather than a typical connectable substation (plain median here = 5405 kW). Applied uniformly to all 9 districts for comparability. Reproducible via scripts/headroom_medians.py. | https://northernpowergrid.opendatasoft.com/
GRID_EXPORT_LIMIT_KW [England E and NE] | DNO export (generation-headroom) connection ceiling - England E and NE [kW] | 13390 | Verified assumption | NPG Heat Map (NE+Yorkshire): MEDIAN OF NON-ZERO headroom across primary substations (n=508, of which 309 at zero = 61%), present-day/2025 basis. Estimator changed from plain median: where a large share of primaries are fully saturated the plain median falls into the zero mass and describes the saturated tail rather than a typical connectable substation (plain median here = 0 kW). Applied uniformly to all 9 districts for comparability. Reproducible via scripts/headroom_medians.py. | https://northernpowergrid.opendatasoft.com/
GRID_IMPORT_LIMIT_KW [England NW and N Wales] | DNO import (demand-headroom) connection ceiling - England NW and N Wales [kW] | 5942.9 | Verified assumption | ENWL NDP + SPEN SPM NSHR pooled: MEDIAN OF NON-ZERO headroom across primary substations (n=729, of which 0 at zero = 0%), present-day/2025 basis. Estimator changed from plain median: where a large share of primaries are fully saturated the plain median falls into the zero mass and describes the saturated tail rather than a typical connectable substation (plain median here = 5920 kW). Applied uniformly to all 9 districts for comparability. Reproducible via scripts/headroom_medians.py. | https://electricitynorthwest.opendatasoft.com/ https://spenergynetworks.opendatasoft.com/
GRID_EXPORT_LIMIT_KW [England NW and N Wales] | DNO export (generation-headroom) connection ceiling - England NW and N Wales [kW] | 25850 | Verified assumption | ENWL NDP only: MEDIAN OF NON-ZERO headroom across primary substations (n=364, of which 0 at zero = 0%), present-day/2025 basis. Estimator changed from plain median: where a large share of primaries are fully saturated the plain median falls into the zero mass and describes the saturated tail rather than a typical connectable substation (plain median here = 25700 kW). Applied uniformly to all 9 districts for comparability. Reproducible via scripts/headroom_medians.py. | https://electricitynorthwest.opendatasoft.com/
GRID_IMPORT_LIMIT_KW [England SE and Central S] | DNO import (demand-headroom) connection ceiling - England SE and Central S [kW] | 8960 | Verified assumption | UKPN DFES NSHR (LPN+SPN) + SSEN SEPD dashboard pooled: MEDIAN OF NON-ZERO headroom across primary substations (n=829, of which 198 at zero = 24%), present-day/2025 basis. Estimator changed from plain median: where a large share of primaries are fully saturated the plain median falls into the zero mass and describes the saturated tail rather than a typical connectable substation (plain median here = 6070 kW). Applied uniformly to all 9 districts for comparability. Reproducible via scripts/headroom_medians.py. | https://ukpowernetworks.opendatasoft.com/explore/dataset/dfes-network-headroom-report/ https://data.ssen.co.uk/
GRID_EXPORT_LIMIT_KW [England SE and Central S] | DNO export (generation-headroom) connection ceiling - England SE and Central S [kW] | 33595 | Verified assumption | UKPN DFES NSHR (LPN+SPN) + SSEN SEPD dashboard pooled: MEDIAN OF NON-ZERO headroom across primary substations (n=823, of which 401 at zero = 49%), present-day/2025 basis. Estimator changed from plain median: where a large share of primaries are fully saturated the plain median falls into the zero mass and describes the saturated tail rather than a typical connectable substation (plain median here = 1610 kW). Applied uniformly to all 9 districts for comparability. Reproducible via scripts/headroom_medians.py. | https://ukpowernetworks.opendatasoft.com/explore/dataset/dfes-network-headroom-report/ https://data.ssen.co.uk/
GRID_IMPORT_LIMIT_KW [England SW and S Wales] | DNO import (demand-headroom) connection ceiling - England SW and S Wales [kW] | 5900 | Verified assumption | NGED Network Capacity Map: MEDIAN OF NON-ZERO headroom across primary substations (n=440, of which 50 at zero = 11%), present-day/2025 basis. Estimator changed from plain median: where a large share of primaries are fully saturated the plain median falls into the zero mass and describes the saturated tail rather than a typical connectable substation (plain median here = 5150 kW). Applied uniformly to all 9 districts for comparability. Reproducible via scripts/headroom_medians.py. | https://connecteddata.nationalgrid.co.uk/dataset/nged-network-capacity
GRID_EXPORT_LIMIT_KW [England SW and S Wales] | DNO export (generation-headroom) connection ceiling - England SW and S Wales [kW] | 8900 | Verified assumption | NGED Network Capacity Map: MEDIAN OF NON-ZERO headroom across primary substations (n=440, of which 75 at zero = 17%), present-day/2025 basis. Estimator changed from plain median: where a large share of primaries are fully saturated the plain median falls into the zero mass and describes the saturated tail rather than a typical connectable substation (plain median here = 6550 kW). Applied uniformly to all 9 districts for comparability. Reproducible via scripts/headroom_medians.py. | https://connecteddata.nationalgrid.co.uk/dataset/nged-network-capacity
GRID_IMPORT_LIMIT_KW [Midlands] | DNO import (demand-headroom) connection ceiling - Midlands [kW] | 7900 | Verified assumption | NGED Network Capacity Map: MEDIAN OF NON-ZERO headroom across primary substations (n=500, of which 23 at zero = 5%), present-day/2025 basis. Estimator changed from plain median: where a large share of primaries are fully saturated the plain median falls into the zero mass and describes the saturated tail rather than a typical connectable substation (plain median here = 7550 kW). Applied uniformly to all 9 districts for comparability. Reproducible via scripts/headroom_medians.py. | https://connecteddata.nationalgrid.co.uk/dataset/nged-network-capacity
GRID_EXPORT_LIMIT_KW [Midlands] | DNO export (generation-headroom) connection ceiling - Midlands [kW] | 14400 | Verified assumption | NGED Network Capacity Map: MEDIAN OF NON-ZERO headroom across primary substations (n=500, of which 58 at zero = 12%), present-day/2025 basis. Estimator changed from plain median: where a large share of primaries are fully saturated the plain median falls into the zero mass and describes the saturated tail rather than a typical connectable substation (plain median here = 12800 kW). Applied uniformly to all 9 districts for comparability. Reproducible via scripts/headroom_medians.py. | https://connecteddata.nationalgrid.co.uk/dataset/nged-network-capacity
GRID_IMPORT_LIMIT_KW [Scotland E] | DNO import (demand-headroom) connection ceiling - Scotland E [kW] | 11362.4 | Verified assumption | SPD NSHR workbook: MEDIAN OF NON-ZERO headroom across primary substations (n=391, of which 0 at zero = 0%), present-day/2025 basis. Estimator changed from plain median: where a large share of primaries are fully saturated the plain median falls into the zero mass and describes the saturated tail rather than a typical connectable substation (plain median here = 11362 kW). Applied uniformly to all 9 districts for comparability. Reproducible via scripts/headroom_medians.py. | https://spenergynetworks.opendatasoft.com/
GRID_EXPORT_LIMIT_KW [Scotland E] | DNO export (generation-headroom) connection ceiling - Scotland E [kW] | 10541 | Verified assumption | SPD NSHR workbook: MEDIAN OF NON-ZERO headroom across primary substations (n=265, of which 39 at zero = 15%), present-day/2025 basis. Estimator changed from plain median: where a large share of primaries are fully saturated the plain median falls into the zero mass and describes the saturated tail rather than a typical connectable substation (plain median here = 9722 kW). Applied uniformly to all 9 districts for comparability. Reproducible via scripts/headroom_medians.py. | https://spenergynetworks.opendatasoft.com/
GRID_IMPORT_LIMIT_KW [Scotland N] | DNO import (demand-headroom) connection ceiling - Scotland N [kW] | 2075 | Verified assumption | SSEN SHEPD dashboard: MEDIAN OF NON-ZERO headroom across primary substations (n=375, of which 169 at zero = 45%), present-day/2025 basis. Estimator changed from plain median: where a large share of primaries are fully saturated the plain median falls into the zero mass and describes the saturated tail rather than a typical connectable substation (plain median here = 110 kW). Applied uniformly to all 9 districts for comparability. Reproducible via scripts/headroom_medians.py. | https://data.ssen.co.uk/
GRID_EXPORT_LIMIT_KW [Scotland N] | DNO export (generation-headroom) connection ceiling - Scotland N [kW] | 1370 | Verified assumption | SSEN SHEPD dashboard: MEDIAN OF NON-ZERO headroom across primary substations (n=375, of which 315 at zero = 84%), present-day/2025 basis. Estimator changed from plain median: where a large share of primaries are fully saturated the plain median falls into the zero mass and describes the saturated tail rather than a typical connectable substation (plain median here = 0 kW). Applied uniformly to all 9 districts for comparability. Reproducible via scripts/headroom_medians.py. | https://data.ssen.co.uk/
GRID_IMPORT_LIMIT_KW [Scotland W] | DNO import (demand-headroom) connection ceiling - Scotland W [kW] | 11362.4 | Verified assumption | SPD NSHR workbook (mirrored from Scotland E): MEDIAN OF NON-ZERO headroom across primary substations (n=391, of which 0 at zero = 0%), present-day/2025 basis. Estimator changed from plain median: where a large share of primaries are fully saturated the plain median falls into the zero mass and describes the saturated tail rather than a typical connectable substation (plain median here = 11362 kW). Applied uniformly to all 9 districts for comparability. Reproducible via scripts/headroom_medians.py. | https://spenergynetworks.opendatasoft.com/
GRID_EXPORT_LIMIT_KW [Scotland W] | DNO export (generation-headroom) connection ceiling - Scotland W [kW] | 10541 | Verified assumption | SPD NSHR workbook (mirrored from Scotland E): MEDIAN OF NON-ZERO headroom across primary substations (n=265, of which 39 at zero = 15%), present-day/2025 basis. Estimator changed from plain median: where a large share of primaries are fully saturated the plain median falls into the zero mass and describes the saturated tail rather than a typical connectable substation (plain median here = 9722 kW). Applied uniformly to all 9 districts for comparability. Reproducible via scripts/headroom_medians.py. | https://spenergynetworks.opendatasoft.com/
GDP_DEFLATOR [2018] | UK GDP deflator index, 2018 (2022=100) | 88.7299 | Verified assumption | DESNZ supplementary guidance, data-tables-1-19.xlsx, Table 19 (UK GDP deflator index). Used to rebase real-terms cost vintages to a common real-2025 basis. | https://www.gov.uk/government/publications/valuation-of-energy-use-and-greenhouse-gas-emissions-for-appraisal
GDP_DEFLATOR [2019] | UK GDP deflator index, 2019 (2022=100) | 90.6061 | Verified assumption | DESNZ supplementary guidance, data-tables-1-19.xlsx, Table 19 (UK GDP deflator index). Used to rebase real-terms cost vintages to a common real-2025 basis. | https://www.gov.uk/government/publications/valuation-of-energy-use-and-greenhouse-gas-emissions-for-appraisal
GDP_DEFLATOR [2020] | UK GDP deflator index, 2020 (2022=100) | 95.4112 | Verified assumption | DESNZ supplementary guidance, data-tables-1-19.xlsx, Table 19 (UK GDP deflator index). Used to rebase real-terms cost vintages to a common real-2025 basis. | https://www.gov.uk/government/publications/valuation-of-energy-use-and-greenhouse-gas-emissions-for-appraisal
GDP_DEFLATOR [2021] | UK GDP deflator index, 2021 (2022=100) | 95.1068 | Verified assumption | DESNZ supplementary guidance, data-tables-1-19.xlsx, Table 19 (UK GDP deflator index). Used to rebase real-terms cost vintages to a common real-2025 basis. | https://www.gov.uk/government/publications/valuation-of-energy-use-and-greenhouse-gas-emissions-for-appraisal
GDP_DEFLATOR [2022] | UK GDP deflator index, 2022 (2022=100) | 100 | Verified assumption | DESNZ supplementary guidance, data-tables-1-19.xlsx, Table 19 (UK GDP deflator index). Used to rebase real-terms cost vintages to a common real-2025 basis. | https://www.gov.uk/government/publications/valuation-of-energy-use-and-greenhouse-gas-emissions-for-appraisal
GDP_DEFLATOR [2023] | UK GDP deflator index, 2023 (2022=100) | 107.0331 | Verified assumption | DESNZ supplementary guidance, data-tables-1-19.xlsx, Table 19 (UK GDP deflator index). Used to rebase real-terms cost vintages to a common real-2025 basis. | https://www.gov.uk/government/publications/valuation-of-energy-use-and-greenhouse-gas-emissions-for-appraisal
GDP_DEFLATOR [2024] | UK GDP deflator index, 2024 (2022=100) | 109.4441 | Verified assumption | DESNZ supplementary guidance, data-tables-1-19.xlsx, Table 19 (UK GDP deflator index). Used to rebase real-terms cost vintages to a common real-2025 basis. | https://www.gov.uk/government/publications/valuation-of-energy-use-and-greenhouse-gas-emissions-for-appraisal
GDP_DEFLATOR [2025] | UK GDP deflator index, 2025 (2022=100) | 111.298 | Verified assumption | DESNZ supplementary guidance, data-tables-1-19.xlsx, Table 19 (UK GDP deflator index). Used to rebase real-terms cost vintages to a common real-2025 basis. | https://www.gov.uk/government/publications/valuation-of-energy-use-and-greenhouse-gas-emissions-for-appraisal
ELEC_DEMAND_TWH [2025] | DESNZ Reference non-heat electricity demand, 2025 [TWh] | 266.711 | Verified assumption | DESNZ Annex F Projections 2023-2050 (final energy demand, Reference scenario): "Total excluding international aviation" / Electricity, TWh. | https://www.gov.uk/government/publications/energy-and-emissions-projections-2023-to-2050
ELEC_DEMAND_TWH [2026] | DESNZ Reference non-heat electricity demand, 2026 [TWh] | 270.358 | Verified assumption | DESNZ Annex F Projections 2023-2050 (final energy demand, Reference scenario): "Total excluding international aviation" / Electricity, TWh. | https://www.gov.uk/government/publications/energy-and-emissions-projections-2023-to-2050
ELEC_DEMAND_TWH [2027] | DESNZ Reference non-heat electricity demand, 2027 [TWh] | 275.331 | Verified assumption | DESNZ Annex F Projections 2023-2050 (final energy demand, Reference scenario): "Total excluding international aviation" / Electricity, TWh. | https://www.gov.uk/government/publications/energy-and-emissions-projections-2023-to-2050
ELEC_DEMAND_TWH [2028] | DESNZ Reference non-heat electricity demand, 2028 [TWh] | 282.205 | Verified assumption | DESNZ Annex F Projections 2023-2050 (final energy demand, Reference scenario): "Total excluding international aviation" / Electricity, TWh. | https://www.gov.uk/government/publications/energy-and-emissions-projections-2023-to-2050
ELEC_DEMAND_TWH [2029] | DESNZ Reference non-heat electricity demand, 2029 [TWh] | 289.979 | Verified assumption | DESNZ Annex F Projections 2023-2050 (final energy demand, Reference scenario): "Total excluding international aviation" / Electricity, TWh. | https://www.gov.uk/government/publications/energy-and-emissions-projections-2023-to-2050
ELEC_DEMAND_TWH [2030] | DESNZ Reference non-heat electricity demand, 2030 [TWh] | 300.4 | Verified assumption | DESNZ Annex F Projections 2023-2050 (final energy demand, Reference scenario): "Total excluding international aviation" / Electricity, TWh. | https://www.gov.uk/government/publications/energy-and-emissions-projections-2023-to-2050
ELEC_DEMAND_TWH [2031] | DESNZ Reference non-heat electricity demand, 2031 [TWh] | 310.073 | Verified assumption | DESNZ Annex F Projections 2023-2050 (final energy demand, Reference scenario): "Total excluding international aviation" / Electricity, TWh. | https://www.gov.uk/government/publications/energy-and-emissions-projections-2023-to-2050
ELEC_DEMAND_TWH [2032] | DESNZ Reference non-heat electricity demand, 2032 [TWh] | 320.251 | Verified assumption | DESNZ Annex F Projections 2023-2050 (final energy demand, Reference scenario): "Total excluding international aviation" / Electricity, TWh. | https://www.gov.uk/government/publications/energy-and-emissions-projections-2023-to-2050
ELEC_DEMAND_TWH [2033] | DESNZ Reference non-heat electricity demand, 2033 [TWh] | 330.283 | Verified assumption | DESNZ Annex F Projections 2023-2050 (final energy demand, Reference scenario): "Total excluding international aviation" / Electricity, TWh. | https://www.gov.uk/government/publications/energy-and-emissions-projections-2023-to-2050
ELEC_DEMAND_TWH [2034] | DESNZ Reference non-heat electricity demand, 2034 [TWh] | 339.854 | Verified assumption | DESNZ Annex F Projections 2023-2050 (final energy demand, Reference scenario): "Total excluding international aviation" / Electricity, TWh. | https://www.gov.uk/government/publications/energy-and-emissions-projections-2023-to-2050
ELEC_DEMAND_TWH [2035] | DESNZ Reference non-heat electricity demand, 2035 [TWh] | 349.344 | Verified assumption | DESNZ Annex F Projections 2023-2050 (final energy demand, Reference scenario): "Total excluding international aviation" / Electricity, TWh. | https://www.gov.uk/government/publications/energy-and-emissions-projections-2023-to-2050
ELEC_DEMAND_TWH [2036] | DESNZ Reference non-heat electricity demand, 2036 [TWh] | 358.618 | Verified assumption | DESNZ Annex F Projections 2023-2050 (final energy demand, Reference scenario): "Total excluding international aviation" / Electricity, TWh. | https://www.gov.uk/government/publications/energy-and-emissions-projections-2023-to-2050
ELEC_DEMAND_TWH [2037] | DESNZ Reference non-heat electricity demand, 2037 [TWh] | 367.869 | Verified assumption | DESNZ Annex F Projections 2023-2050 (final energy demand, Reference scenario): "Total excluding international aviation" / Electricity, TWh. | https://www.gov.uk/government/publications/energy-and-emissions-projections-2023-to-2050
ELEC_DEMAND_TWH [2038] | DESNZ Reference non-heat electricity demand, 2038 [TWh] | 377.218 | Verified assumption | DESNZ Annex F Projections 2023-2050 (final energy demand, Reference scenario): "Total excluding international aviation" / Electricity, TWh. | https://www.gov.uk/government/publications/energy-and-emissions-projections-2023-to-2050
ELEC_DEMAND_TWH [2039] | DESNZ Reference non-heat electricity demand, 2039 [TWh] | 385.067 | Verified assumption | DESNZ Annex F Projections 2023-2050 (final energy demand, Reference scenario): "Total excluding international aviation" / Electricity, TWh. | https://www.gov.uk/government/publications/energy-and-emissions-projections-2023-to-2050
ELEC_DEMAND_TWH [2040] | DESNZ Reference non-heat electricity demand, 2040 [TWh] | 392.379 | Verified assumption | DESNZ Annex F Projections 2023-2050 (final energy demand, Reference scenario): "Total excluding international aviation" / Electricity, TWh. | https://www.gov.uk/government/publications/energy-and-emissions-projections-2023-to-2050
ELEC_DEMAND_TWH [2041] | DESNZ Reference non-heat electricity demand, 2041 [TWh] | 400.007 | Verified assumption | DESNZ Annex F Projections 2023-2050 (final energy demand, Reference scenario): "Total excluding international aviation" / Electricity, TWh. | https://www.gov.uk/government/publications/energy-and-emissions-projections-2023-to-2050
ELEC_DEMAND_TWH [2042] | DESNZ Reference non-heat electricity demand, 2042 [TWh] | 406.547 | Verified assumption | DESNZ Annex F Projections 2023-2050 (final energy demand, Reference scenario): "Total excluding international aviation" / Electricity, TWh. | https://www.gov.uk/government/publications/energy-and-emissions-projections-2023-to-2050
ELEC_DEMAND_TWH [2043] | DESNZ Reference non-heat electricity demand, 2043 [TWh] | 412.686 | Verified assumption | DESNZ Annex F Projections 2023-2050 (final energy demand, Reference scenario): "Total excluding international aviation" / Electricity, TWh. | https://www.gov.uk/government/publications/energy-and-emissions-projections-2023-to-2050
ELEC_DEMAND_TWH [2044] | DESNZ Reference non-heat electricity demand, 2044 [TWh] | 418.812 | Verified assumption | DESNZ Annex F Projections 2023-2050 (final energy demand, Reference scenario): "Total excluding international aviation" / Electricity, TWh. | https://www.gov.uk/government/publications/energy-and-emissions-projections-2023-to-2050
ELEC_DEMAND_TWH [2045] | DESNZ Reference non-heat electricity demand, 2045 [TWh] | 424.623 | Verified assumption | DESNZ Annex F Projections 2023-2050 (final energy demand, Reference scenario): "Total excluding international aviation" / Electricity, TWh. | https://www.gov.uk/government/publications/energy-and-emissions-projections-2023-to-2050
ELEC_DEMAND_TWH [2046] | DESNZ Reference non-heat electricity demand, 2046 [TWh] | 430.18 | Verified assumption | DESNZ Annex F Projections 2023-2050 (final energy demand, Reference scenario): "Total excluding international aviation" / Electricity, TWh. | https://www.gov.uk/government/publications/energy-and-emissions-projections-2023-to-2050
ELEC_DEMAND_TWH [2047] | DESNZ Reference non-heat electricity demand, 2047 [TWh] | 435.493 | Verified assumption | DESNZ Annex F Projections 2023-2050 (final energy demand, Reference scenario): "Total excluding international aviation" / Electricity, TWh. | https://www.gov.uk/government/publications/energy-and-emissions-projections-2023-to-2050
ELEC_DEMAND_TWH [2048] | DESNZ Reference non-heat electricity demand, 2048 [TWh] | 440.692 | Verified assumption | DESNZ Annex F Projections 2023-2050 (final energy demand, Reference scenario): "Total excluding international aviation" / Electricity, TWh. | https://www.gov.uk/government/publications/energy-and-emissions-projections-2023-to-2050
ELEC_DEMAND_TWH [2049] | DESNZ Reference non-heat electricity demand, 2049 [TWh] | 445.576 | Verified assumption | DESNZ Annex F Projections 2023-2050 (final energy demand, Reference scenario): "Total excluding international aviation" / Electricity, TWh. | https://www.gov.uk/government/publications/energy-and-emissions-projections-2023-to-2050
ELEC_DEMAND_TWH [2050] | DESNZ Reference non-heat electricity demand, 2050 [TWh] | 450.338 | Verified assumption | DESNZ Annex F Projections 2023-2050 (final energy demand, Reference scenario): "Total excluding international aviation" / Electricity, TWh. | https://www.gov.uk/government/publications/energy-and-emissions-projections-2023-to-2050

## Energy Prices
Group | Key | Active | Min (MWh/yr) | Max (MWh/yr) | Parameter | Description (units) | Value | Type | Source | Source URL
Gas Import | Very Small |  | 0 | 278 | gas_import_price | Non-domestic gas import price, Very Small band [GBP/kWh, incl CCL] | 0.0829 | Verified assumption | DESNZ Quarterly Energy Prices, Table 3.4.2 (non-domestic gas, annual 2025, incl CCL, excl VAT) - March 2026 | https://www.gov.uk/government/statistical-data-sets/gas-and-electricity-prices-in-the-non-domestic-sector
Gas Import | Small |  | 278 | 2778 | gas_import_price | Non-domestic gas import price, Small band [GBP/kWh, incl CCL] | 0.0513 | Verified assumption | DESNZ Quarterly Energy Prices, Table 3.4.2 (non-domestic gas, annual 2025, incl CCL, excl VAT) - March 2026 | https://www.gov.uk/government/statistical-data-sets/gas-and-electricity-prices-in-the-non-domestic-sector
Gas Import | Medium |  | 2778 | 27778 | gas_import_price | Non-domestic gas import price, Medium band [GBP/kWh, incl CCL] | 0.0468 | Verified assumption | DESNZ Quarterly Energy Prices, Table 3.4.2 (non-domestic gas, annual 2025, incl CCL, excl VAT) - March 2026 | https://www.gov.uk/government/statistical-data-sets/gas-and-electricity-prices-in-the-non-domestic-sector
Gas Import | Large |  | 27778 | 277778 | gas_import_price | Non-domestic gas import price, Large band [GBP/kWh, incl CCL] | 0.0415 | Verified assumption | DESNZ Quarterly Energy Prices, Table 3.4.2 (non-domestic gas, annual 2025, incl CCL, excl VAT) - March 2026 | https://www.gov.uk/government/statistical-data-sets/gas-and-electricity-prices-in-the-non-domestic-sector
Gas Import | Very Large |  | 277778 | 1111112 | gas_import_price | Non-domestic gas import price, Very Large band [GBP/kWh, incl CCL] | 0.0422 | Verified assumption | DESNZ Quarterly Energy Prices, Table 3.4.2 (non-domestic gas, annual 2025, incl CCL, excl VAT) - March 2026 | https://www.gov.uk/government/statistical-data-sets/gas-and-electricity-prices-in-the-non-domestic-sector
Electricity Import | Very Small |  | 0 | 20 | elec_import_price | Non-domestic electricity import price, Very Small band [GBP/kWh, incl CCL] | 0.34929 | Verified assumption | DESNZ Quarterly Energy Prices, Table 3.4.2 (non-domestic electricity, annual 2025, incl CCL, excl VAT) - March 2026 | https://www.gov.uk/government/statistical-data-sets/gas-and-electricity-prices-in-the-non-domestic-sector
Electricity Import | Small |  | 20 | 500 | elec_import_price | Non-domestic electricity import price, Small band [GBP/kWh, incl CCL] | 0.29092 | Verified assumption | DESNZ Quarterly Energy Prices, Table 3.4.2 (non-domestic electricity, annual 2025, incl CCL, excl VAT) - March 2026 | https://www.gov.uk/government/statistical-data-sets/gas-and-electricity-prices-in-the-non-domestic-sector
Electricity Import | Small/Medium |  | 500 | 2000 | elec_import_price | Non-domestic electricity import price, Small/Medium band [GBP/kWh, incl CCL] | 0.28246 | Verified assumption | DESNZ Quarterly Energy Prices, Table 3.4.2 (non-domestic electricity, annual 2025, incl CCL, excl VAT) - March 2026 | https://www.gov.uk/government/statistical-data-sets/gas-and-electricity-prices-in-the-non-domestic-sector
Electricity Import | Medium |  | 2000 | 20000 | elec_import_price | Non-domestic electricity import price, Medium band [GBP/kWh, incl CCL] | 0.25905 | Verified assumption | DESNZ Quarterly Energy Prices, Table 3.4.2 (non-domestic electricity, annual 2025, incl CCL, excl VAT) - March 2026 | https://www.gov.uk/government/statistical-data-sets/gas-and-electricity-prices-in-the-non-domestic-sector
Electricity Import | Large |  | 20000 | 70000 | elec_import_price | Non-domestic electricity import price, Large band [GBP/kWh, incl CCL] | 0.24401 | Verified assumption | DESNZ Quarterly Energy Prices, Table 3.4.2 (non-domestic electricity, annual 2025, incl CCL, excl VAT) - March 2026 | https://www.gov.uk/government/statistical-data-sets/gas-and-electricity-prices-in-the-non-domestic-sector
Electricity Import | Very Large |  | 70000 | 150000 | elec_import_price | Non-domestic electricity import price, Very Large band [GBP/kWh, incl CCL] | 0.22095 | Verified assumption | DESNZ Quarterly Energy Prices, Table 3.4.2 (non-domestic electricity, annual 2025, incl CCL, excl VAT) - March 2026 | https://www.gov.uk/government/statistical-data-sets/gas-and-electricity-prices-in-the-non-domestic-sector
Electricity Import | Extra Large |  | 150000 |  | elec_import_price | Non-domestic electricity import price, Extra Large band [GBP/kWh, incl CCL] | 0.21379 | Verified assumption | DESNZ Quarterly Energy Prices, Table 3.4.2 (non-domestic electricity, annual 2025, incl CCL, excl VAT) - March 2026 | https://www.gov.uk/government/statistical-data-sets/gas-and-electricity-prices-in-the-non-domestic-sector
Electricity Export | Low |  |  |  | elec_export_price | SEG export price - low sensitivity [GBP/kWh] | 0.05 | Verified assumption | Ofgem Smart Export Guarantee tariff tables; supplier SEG rates (British Gas, EDF, Good Energy, ScottishPower) up to 5 MW, June 2026. Low/central/high sensitivity set. | https://solarenergyuk.org/resource/smart-export-guarantee/
Electricity Export | Central | yes |  |  | elec_export_price | SEG export price - central [GBP/kWh] | 0.1 | Verified assumption | Ofgem Smart Export Guarantee tariff tables; supplier SEG rates (British Gas, EDF, Good Energy, ScottishPower) up to 5 MW, June 2026. Low/central/high sensitivity set. | https://solarenergyuk.org/resource/smart-export-guarantee/
Electricity Export | High |  |  |  | elec_export_price | SEG export price - high sensitivity [GBP/kWh] | 0.15 | Verified assumption | Ofgem Smart Export Guarantee tariff tables; supplier SEG rates (British Gas, EDF, Good Energy, ScottishPower) up to 5 MW, June 2026. Low/central/high sensitivity set. | https://solarenergyuk.org/resource/smart-export-guarantee/
Energy Price Growth | Low |  |  |  | elec_price_growth | Electricity price real escalation - DESNZ Low [/yr] | -2.98% | Verified assumption | DESNZ supplementary guidance, data-tables-1-19.xlsx Table 4 (electricity) / 5 (gas), Commercial/Public sector, real 2022 prices. All escalation anchored to Central 2025, diverging to DESNZ's 2040 Low/Central/High values. | https://www.gov.uk/government/publications/valuation-of-energy-use-and-greenhouse-gas-emissions-for-appraisal
Energy Price Growth | Central | yes |  |  | elec_price_growth | Electricity price real escalation - DESNZ Central [/yr] | -2.7% | Verified assumption | DESNZ supplementary guidance, data-tables-1-19.xlsx Table 4 (electricity) / 5 (gas), Commercial/Public sector, real 2022 prices. All escalation anchored to Central 2025, diverging to DESNZ's 2040 Low/Central/High values. | https://www.gov.uk/government/publications/valuation-of-energy-use-and-greenhouse-gas-emissions-for-appraisal
Energy Price Growth | High |  |  |  | elec_price_growth | Electricity price real escalation - DESNZ High [/yr] | -2.21% | Verified assumption | DESNZ supplementary guidance, data-tables-1-19.xlsx Table 4 (electricity) / 5 (gas), Commercial/Public sector, real 2022 prices. All escalation anchored to Central 2025, diverging to DESNZ's 2040 Low/Central/High values. | https://www.gov.uk/government/publications/valuation-of-energy-use-and-greenhouse-gas-emissions-for-appraisal
Energy Price Growth | Low |  |  |  | gas_price_growth | Gas price real escalation - DESNZ Low [/yr] | -5.57% | Verified assumption | DESNZ supplementary guidance, data-tables-1-19.xlsx Table 4 (electricity) / 5 (gas), Commercial/Public sector, real 2022 prices. All escalation anchored to Central 2025, diverging to DESNZ's 2040 Low/Central/High values. | https://www.gov.uk/government/publications/valuation-of-energy-use-and-greenhouse-gas-emissions-for-appraisal
Energy Price Growth | Central | yes |  |  | gas_price_growth | Gas price real escalation - DESNZ Central [/yr] | -1.7% | Verified assumption | DESNZ supplementary guidance, data-tables-1-19.xlsx Table 4 (electricity) / 5 (gas), Commercial/Public sector, real 2022 prices. All escalation anchored to Central 2025, diverging to DESNZ's 2040 Low/Central/High values. | https://www.gov.uk/government/publications/valuation-of-energy-use-and-greenhouse-gas-emissions-for-appraisal
Energy Price Growth | High |  |  |  | gas_price_growth | Gas price real escalation - DESNZ High [/yr] | 2.25% | Verified assumption | DESNZ supplementary guidance, data-tables-1-19.xlsx Table 4 (electricity) / 5 (gas), Commercial/Public sector, real 2022 prices. All escalation anchored to Central 2025, diverging to DESNZ's 2040 Low/Central/High values. | https://www.gov.uk/government/publications/valuation-of-energy-use-and-greenhouse-gas-emissions-for-appraisal
Import Price Scenario | Low |  |  |  | elec_import_multiplier | Electricity import price level multiplier - low sensitivity [x Central 2025 band price] | 66.56% | Verified assumption | DESNZ supplementary guidance, data-tables-1-19.xlsx, Tables 4 (electricity) & 5 (gas), Commercial/Public sector, real 2022 prices. | https://www.gov.uk/government/publications/valuation-of-energy-use-and-greenhouse-gas-emissions-for-appraisal
Import Price Scenario | Central | yes |  |  | elec_import_multiplier | Electricity import price level multiplier - central (= DESNZ Quarterly 2025 band actuals) [x] | 100% | Verified assumption | DESNZ supplementary guidance, data-tables-1-19.xlsx, Tables 4 (electricity) & 5 (gas), Commercial/Public sector, real 2022 prices. | https://www.gov.uk/government/publications/valuation-of-energy-use-and-greenhouse-gas-emissions-for-appraisal
Import Price Scenario | High |  |  |  | elec_import_multiplier | Electricity import price level multiplier - high sensitivity [x Central 2025 band price] | 226.8% | Verified assumption | DESNZ supplementary guidance, data-tables-1-19.xlsx, Tables 4 (electricity) & 5 (gas), Commercial/Public sector, real 2022 prices. | https://www.gov.uk/government/publications/valuation-of-energy-use-and-greenhouse-gas-emissions-for-appraisal
Import Price Scenario | Low |  |  |  | gas_import_multiplier | Gas import price level multiplier - low sensitivity [x Central 2025 band price] | 51.45% | Verified assumption | DESNZ supplementary guidance, data-tables-1-19.xlsx, Tables 4 (electricity) & 5 (gas), Commercial/Public sector, real 2022 prices. | https://www.gov.uk/government/publications/valuation-of-energy-use-and-greenhouse-gas-emissions-for-appraisal
Import Price Scenario | Central | yes |  |  | gas_import_multiplier | Gas import price level multiplier - central (= DESNZ Quarterly 2025 band actuals) [x] | 100% | Verified assumption | DESNZ supplementary guidance, data-tables-1-19.xlsx, Tables 4 (electricity) & 5 (gas), Commercial/Public sector, real 2022 prices. | https://www.gov.uk/government/publications/valuation-of-energy-use-and-greenhouse-gas-emissions-for-appraisal
Import Price Scenario | High |  |  |  | gas_import_multiplier | Gas import price level multiplier - high sensitivity [x Central 2025 band price] | 287.4% | Verified assumption | DESNZ supplementary guidance, data-tables-1-19.xlsx, Tables 4 (electricity) & 5 (gas), Commercial/Public sector, real 2022 prices. | https://www.gov.uk/government/publications/valuation-of-energy-use-and-greenhouse-gas-emissions-for-appraisal
Retail Non-Commodity | CCL |  |  |  | ccl | Climate Change Levy, electricity main rate [GBP/kWh] | 0.00801 | Verified assumption | HMRC/GOV.UK Climate Change Levy main rates. GBP 0.00801/kWh from 1 Apr 2026 (elec & gas aligned) - used to build up electricity tariff | https://www.gov.uk/guidance/climate-change-levy-rates
DUoS Time Band | East Anglia |  |  |  | duos_red_start_h | DUoS Red band start, weekday [h, 24h decimal] | 16 | Verified assumption | Eastern Power Networks (UKPN EPN) 2025 Schedule of Charges, Annex 1 'Time Bands for LV and HV Designated Properties'. File: eastern-power-networks-schedule-of-charges-and-other-tables-2025-v1-9.xlsx | https://www.ukpowernetworks.co.uk/our-company/distribution-use-of-system-charges
DUoS Time Band | East Anglia |  |  |  | duos_red_end_h | DUoS Red band end, weekday [h] | 19 | Verified assumption | Eastern Power Networks (UKPN EPN) 2025 Schedule of Charges, Annex 1 'Time Bands for LV and HV Designated Properties'. File: eastern-power-networks-schedule-of-charges-and-other-tables-2025-v1-9.xlsx | https://www.ukpowernetworks.co.uk/our-company/distribution-use-of-system-charges
DUoS Time Band | East Anglia |  |  |  | duos_amber_am_start_h | DUoS Amber morning band start, weekday [h] | 7 | Verified assumption | Eastern Power Networks (UKPN EPN) 2025 Schedule of Charges, Annex 1 'Time Bands for LV and HV Designated Properties'. File: eastern-power-networks-schedule-of-charges-and-other-tables-2025-v1-9.xlsx | https://www.ukpowernetworks.co.uk/our-company/distribution-use-of-system-charges
DUoS Time Band | East Anglia |  |  |  | duos_amber_am_end_h | DUoS Amber morning band end, weekday [h] | 16 | Verified assumption | Eastern Power Networks (UKPN EPN) 2025 Schedule of Charges, Annex 1 'Time Bands for LV and HV Designated Properties'. File: eastern-power-networks-schedule-of-charges-and-other-tables-2025-v1-9.xlsx | https://www.ukpowernetworks.co.uk/our-company/distribution-use-of-system-charges
DUoS Time Band | East Anglia |  |  |  | duos_amber_pm_start_h | DUoS Amber evening band start, weekday [h] | 19 | Verified assumption | Eastern Power Networks (UKPN EPN) 2025 Schedule of Charges, Annex 1 'Time Bands for LV and HV Designated Properties'. File: eastern-power-networks-schedule-of-charges-and-other-tables-2025-v1-9.xlsx | https://www.ukpowernetworks.co.uk/our-company/distribution-use-of-system-charges
DUoS Time Band | East Anglia |  |  |  | duos_amber_pm_end_h | DUoS Amber evening band end, weekday [h] | 23 | Verified assumption | Eastern Power Networks (UKPN EPN) 2025 Schedule of Charges, Annex 1 'Time Bands for LV and HV Designated Properties'. File: eastern-power-networks-schedule-of-charges-and-other-tables-2025-v1-9.xlsx | https://www.ukpowernetworks.co.uk/our-company/distribution-use-of-system-charges
DUoS Time Band | East Anglia |  |  |  | duos_we_amber_start_h | DUoS Amber band start, weekend; 0 = none (all Green) [h] | 0 | Verified assumption | Eastern Power Networks (UKPN EPN) 2025 Schedule of Charges, Annex 1 'Time Bands for LV and HV Designated Properties'. File: eastern-power-networks-schedule-of-charges-and-other-tables-2025-v1-9.xlsx | https://www.ukpowernetworks.co.uk/our-company/distribution-use-of-system-charges
DUoS Time Band | East Anglia |  |  |  | duos_we_amber_end_h | DUoS Amber band end, weekend; 0 = none (all Green) [h] | 0 | Verified assumption | Eastern Power Networks (UKPN EPN) 2025 Schedule of Charges, Annex 1 'Time Bands for LV and HV Designated Properties'. File: eastern-power-networks-schedule-of-charges-and-other-tables-2025-v1-9.xlsx | https://www.ukpowernetworks.co.uk/our-company/distribution-use-of-system-charges
DUoS Time Band | England E and NE |  |  |  | duos_red_start_h | DUoS Red band start, weekday [h, 24h decimal] | 16 | Verified assumption | Northern Powergrid (Northeast) 2025-26 Schedule of Charges, Annex 1 time bands. File: Northern Powergrid (Northeast) - 2025-26 Schedule of charges and other tables v0.2.xlsx | https://www.northernpowergrid.com/node/1526
DUoS Time Band | England E and NE |  |  |  | duos_red_end_h | DUoS Red band end, weekday [h] | 19.5 | Verified assumption | Northern Powergrid (Northeast) 2025-26 Schedule of Charges, Annex 1 time bands. File: Northern Powergrid (Northeast) - 2025-26 Schedule of charges and other tables v0.2.xlsx | https://www.northernpowergrid.com/node/1526
DUoS Time Band | England E and NE |  |  |  | duos_amber_am_start_h | DUoS Amber morning band start, weekday [h] | 8 | Verified assumption | Northern Powergrid (Northeast) 2025-26 Schedule of Charges, Annex 1 time bands. File: Northern Powergrid (Northeast) - 2025-26 Schedule of charges and other tables v0.2.xlsx | https://www.northernpowergrid.com/node/1526
DUoS Time Band | England E and NE |  |  |  | duos_amber_am_end_h | DUoS Amber morning band end, weekday [h] | 16 | Verified assumption | Northern Powergrid (Northeast) 2025-26 Schedule of Charges, Annex 1 time bands. File: Northern Powergrid (Northeast) - 2025-26 Schedule of charges and other tables v0.2.xlsx | https://www.northernpowergrid.com/node/1526
DUoS Time Band | England E and NE |  |  |  | duos_amber_pm_start_h | DUoS Amber evening band start, weekday [h] | 19.5 | Verified assumption | Northern Powergrid (Northeast) 2025-26 Schedule of Charges, Annex 1 time bands. File: Northern Powergrid (Northeast) - 2025-26 Schedule of charges and other tables v0.2.xlsx | https://www.northernpowergrid.com/node/1526
DUoS Time Band | England E and NE |  |  |  | duos_amber_pm_end_h | DUoS Amber evening band end, weekday [h] | 22 | Verified assumption | Northern Powergrid (Northeast) 2025-26 Schedule of Charges, Annex 1 time bands. File: Northern Powergrid (Northeast) - 2025-26 Schedule of charges and other tables v0.2.xlsx | https://www.northernpowergrid.com/node/1526
DUoS Time Band | England E and NE |  |  |  | duos_we_amber_start_h | DUoS Amber band start, weekend; 0 = none (all Green) [h] | 0 | Verified assumption | Northern Powergrid (Northeast) 2025-26 Schedule of Charges, Annex 1 time bands. File: Northern Powergrid (Northeast) - 2025-26 Schedule of charges and other tables v0.2.xlsx | https://www.northernpowergrid.com/node/1526
DUoS Time Band | England E and NE |  |  |  | duos_we_amber_end_h | DUoS Amber band end, weekend; 0 = none (all Green) [h] | 0 | Verified assumption | Northern Powergrid (Northeast) 2025-26 Schedule of Charges, Annex 1 time bands. File: Northern Powergrid (Northeast) - 2025-26 Schedule of charges and other tables v0.2.xlsx | https://www.northernpowergrid.com/node/1526
DUoS Time Band | England NW and N Wales |  |  |  | duos_red_start_h | DUoS Red band start, weekday [h, 24h decimal] | 16 | Verified assumption | Electricity North West (ENWL) 2025 Schedule of Charges, Annex 1 time bands. File: enwl---schedule-of-charges-and-other-tables--2025-v2_0.xlsx | https://www.enwl.co.uk/about-us/regulatory-information/use-of-system-charges/current-charging-information/
DUoS Time Band | England NW and N Wales |  |  |  | duos_red_end_h | DUoS Red band end, weekday [h] | 19 | Verified assumption | Electricity North West (ENWL) 2025 Schedule of Charges, Annex 1 time bands. File: enwl---schedule-of-charges-and-other-tables--2025-v2_0.xlsx | https://www.enwl.co.uk/about-us/regulatory-information/use-of-system-charges/current-charging-information/
DUoS Time Band | England NW and N Wales |  |  |  | duos_amber_am_start_h | DUoS Amber morning band start, weekday [h] | 9 | Verified assumption | Electricity North West (ENWL) 2025 Schedule of Charges, Annex 1 time bands. File: enwl---schedule-of-charges-and-other-tables--2025-v2_0.xlsx | https://www.enwl.co.uk/about-us/regulatory-information/use-of-system-charges/current-charging-information/
DUoS Time Band | England NW and N Wales |  |  |  | duos_amber_am_end_h | DUoS Amber morning band end, weekday [h] | 16 | Verified assumption | Electricity North West (ENWL) 2025 Schedule of Charges, Annex 1 time bands. File: enwl---schedule-of-charges-and-other-tables--2025-v2_0.xlsx | https://www.enwl.co.uk/about-us/regulatory-information/use-of-system-charges/current-charging-information/
DUoS Time Band | England NW and N Wales |  |  |  | duos_amber_pm_start_h | DUoS Amber evening band start, weekday [h] | 19 | Verified assumption | Electricity North West (ENWL) 2025 Schedule of Charges, Annex 1 time bands. File: enwl---schedule-of-charges-and-other-tables--2025-v2_0.xlsx | https://www.enwl.co.uk/about-us/regulatory-information/use-of-system-charges/current-charging-information/
DUoS Time Band | England NW and N Wales |  |  |  | duos_amber_pm_end_h | DUoS Amber evening band end, weekday [h] | 20.5 | Verified assumption | Electricity North West (ENWL) 2025 Schedule of Charges, Annex 1 time bands. File: enwl---schedule-of-charges-and-other-tables--2025-v2_0.xlsx | https://www.enwl.co.uk/about-us/regulatory-information/use-of-system-charges/current-charging-information/
DUoS Time Band | England NW and N Wales |  |  |  | duos_we_amber_start_h | DUoS Amber band start, weekend; 0 = none (all Green) [h] | 16 | Verified assumption | Electricity North West (ENWL) 2025 Schedule of Charges, Annex 1 time bands. File: enwl---schedule-of-charges-and-other-tables--2025-v2_0.xlsx | https://www.enwl.co.uk/about-us/regulatory-information/use-of-system-charges/current-charging-information/
DUoS Time Band | England NW and N Wales |  |  |  | duos_we_amber_end_h | DUoS Amber band end, weekend; 0 = none (all Green) [h] | 19 | Verified assumption | Electricity North West (ENWL) 2025 Schedule of Charges, Annex 1 time bands. File: enwl---schedule-of-charges-and-other-tables--2025-v2_0.xlsx | https://www.enwl.co.uk/about-us/regulatory-information/use-of-system-charges/current-charging-information/
DUoS Time Band | England SE and Central S |  |  |  | duos_red_start_h | DUoS Red band start, weekday [h, 24h decimal] | 16.5 | Verified assumption | SSEN Southern Electric Power Distribution (SEPD) April 2025 Schedule of Charges, Annex 1 time bands. File: sepd---schedule-of-charges-and-other-tables---april-2025-v0.3.xlsx | https://www.ssen.co.uk/about-ssen/library/charging-statements-and-information/southern-electric-power-distribution/
DUoS Time Band | England SE and Central S |  |  |  | duos_red_end_h | DUoS Red band end, weekday [h] | 19.5 | Verified assumption | SSEN Southern Electric Power Distribution (SEPD) April 2025 Schedule of Charges, Annex 1 time bands. File: sepd---schedule-of-charges-and-other-tables---april-2025-v0.3.xlsx | https://www.ssen.co.uk/about-ssen/library/charging-statements-and-information/southern-electric-power-distribution/
DUoS Time Band | England SE and Central S |  |  |  | duos_amber_am_start_h | DUoS Amber morning band start, weekday [h] | 7 | Verified assumption | SSEN Southern Electric Power Distribution (SEPD) April 2025 Schedule of Charges, Annex 1 time bands. File: sepd---schedule-of-charges-and-other-tables---april-2025-v0.3.xlsx | https://www.ssen.co.uk/about-ssen/library/charging-statements-and-information/southern-electric-power-distribution/
DUoS Time Band | England SE and Central S |  |  |  | duos_amber_am_end_h | DUoS Amber morning band end, weekday [h] | 16.5 | Verified assumption | SSEN Southern Electric Power Distribution (SEPD) April 2025 Schedule of Charges, Annex 1 time bands. File: sepd---schedule-of-charges-and-other-tables---april-2025-v0.3.xlsx | https://www.ssen.co.uk/about-ssen/library/charging-statements-and-information/southern-electric-power-distribution/
DUoS Time Band | England SE and Central S |  |  |  | duos_amber_pm_start_h | DUoS Amber evening band start, weekday [h] | 19.5 | Verified assumption | SSEN Southern Electric Power Distribution (SEPD) April 2025 Schedule of Charges, Annex 1 time bands. File: sepd---schedule-of-charges-and-other-tables---april-2025-v0.3.xlsx | https://www.ssen.co.uk/about-ssen/library/charging-statements-and-information/southern-electric-power-distribution/
DUoS Time Band | England SE and Central S |  |  |  | duos_amber_pm_end_h | DUoS Amber evening band end, weekday [h] | 22 | Verified assumption | SSEN Southern Electric Power Distribution (SEPD) April 2025 Schedule of Charges, Annex 1 time bands. File: sepd---schedule-of-charges-and-other-tables---april-2025-v0.3.xlsx | https://www.ssen.co.uk/about-ssen/library/charging-statements-and-information/southern-electric-power-distribution/
DUoS Time Band | England SE and Central S |  |  |  | duos_we_amber_start_h | DUoS Amber band start, weekend; 0 = none (all Green) [h] | 9.5 | Verified assumption | SSEN Southern Electric Power Distribution (SEPD) April 2025 Schedule of Charges, Annex 1 time bands. File: sepd---schedule-of-charges-and-other-tables---april-2025-v0.3.xlsx | https://www.ssen.co.uk/about-ssen/library/charging-statements-and-information/southern-electric-power-distribution/
DUoS Time Band | England SE and Central S |  |  |  | duos_we_amber_end_h | DUoS Amber band end, weekend; 0 = none (all Green) [h] | 21.5 | Verified assumption | SSEN Southern Electric Power Distribution (SEPD) April 2025 Schedule of Charges, Annex 1 time bands. File: sepd---schedule-of-charges-and-other-tables---april-2025-v0.3.xlsx | https://www.ssen.co.uk/about-ssen/library/charging-statements-and-information/southern-electric-power-distribution/
DUoS Time Band | England SW and S Wales |  |  |  | duos_red_start_h | DUoS Red band start, weekday [h, 24h decimal] | 17 | Verified assumption | National Grid Electricity Distribution South West (SWEB) 2025 Schedule of Charges, Annex 1 time bands. File: SWEB - Schedule of charges and other tables- 2025 V.0.1 for publishing.xlsx | https://commercial.nationalgrid.co.uk/our-network/use-of-system-charges/charging-statements-and-methodology
DUoS Time Band | England SW and S Wales |  |  |  | duos_red_end_h | DUoS Red band end, weekday [h] | 19 | Verified assumption | National Grid Electricity Distribution South West (SWEB) 2025 Schedule of Charges, Annex 1 time bands. File: SWEB - Schedule of charges and other tables- 2025 V.0.1 for publishing.xlsx | https://commercial.nationalgrid.co.uk/our-network/use-of-system-charges/charging-statements-and-methodology
DUoS Time Band | England SW and S Wales |  |  |  | duos_amber_am_start_h | DUoS Amber morning band start, weekday [h] | 7.5 | Verified assumption | National Grid Electricity Distribution South West (SWEB) 2025 Schedule of Charges, Annex 1 time bands. File: SWEB - Schedule of charges and other tables- 2025 V.0.1 for publishing.xlsx | https://commercial.nationalgrid.co.uk/our-network/use-of-system-charges/charging-statements-and-methodology
DUoS Time Band | England SW and S Wales |  |  |  | duos_amber_am_end_h | DUoS Amber morning band end, weekday [h] | 17 | Verified assumption | National Grid Electricity Distribution South West (SWEB) 2025 Schedule of Charges, Annex 1 time bands. File: SWEB - Schedule of charges and other tables- 2025 V.0.1 for publishing.xlsx | https://commercial.nationalgrid.co.uk/our-network/use-of-system-charges/charging-statements-and-methodology
DUoS Time Band | England SW and S Wales |  |  |  | duos_amber_pm_start_h | DUoS Amber evening band start, weekday [h] | 19 | Verified assumption | National Grid Electricity Distribution South West (SWEB) 2025 Schedule of Charges, Annex 1 time bands. File: SWEB - Schedule of charges and other tables- 2025 V.0.1 for publishing.xlsx | https://commercial.nationalgrid.co.uk/our-network/use-of-system-charges/charging-statements-and-methodology
DUoS Time Band | England SW and S Wales |  |  |  | duos_amber_pm_end_h | DUoS Amber evening band end, weekday [h] | 21.5 | Verified assumption | National Grid Electricity Distribution South West (SWEB) 2025 Schedule of Charges, Annex 1 time bands. File: SWEB - Schedule of charges and other tables- 2025 V.0.1 for publishing.xlsx | https://commercial.nationalgrid.co.uk/our-network/use-of-system-charges/charging-statements-and-methodology
DUoS Time Band | England SW and S Wales |  |  |  | duos_we_amber_start_h | DUoS Amber band start, weekend; 0 = none (all Green) [h] | 16.5 | Verified assumption | National Grid Electricity Distribution South West (SWEB) 2025 Schedule of Charges, Annex 1 time bands. File: SWEB - Schedule of charges and other tables- 2025 V.0.1 for publishing.xlsx | https://commercial.nationalgrid.co.uk/our-network/use-of-system-charges/charging-statements-and-methodology
DUoS Time Band | England SW and S Wales |  |  |  | duos_we_amber_end_h | DUoS Amber band end, weekend; 0 = none (all Green) [h] | 19.5 | Verified assumption | National Grid Electricity Distribution South West (SWEB) 2025 Schedule of Charges, Annex 1 time bands. File: SWEB - Schedule of charges and other tables- 2025 V.0.1 for publishing.xlsx | https://commercial.nationalgrid.co.uk/our-network/use-of-system-charges/charging-statements-and-methodology
DUoS Time Band | Midlands |  |  |  | duos_red_start_h | DUoS Red band start, weekday [h, 24h decimal] | 16 | Verified assumption | National Grid Electricity Distribution West Midlands (MIDE) 2025 Schedule of Charges, Annex 1 time bands. File: MIDE - Schedule of charges and other tables- 2025 V.0.1 for publishing.xlsx | https://commercial.nationalgrid.co.uk/our-network/use-of-system-charges/charging-statements-and-methodology
DUoS Time Band | Midlands |  |  |  | duos_red_end_h | DUoS Red band end, weekday [h] | 19 | Verified assumption | National Grid Electricity Distribution West Midlands (MIDE) 2025 Schedule of Charges, Annex 1 time bands. File: MIDE - Schedule of charges and other tables- 2025 V.0.1 for publishing.xlsx | https://commercial.nationalgrid.co.uk/our-network/use-of-system-charges/charging-statements-and-methodology
DUoS Time Band | Midlands |  |  |  | duos_amber_am_start_h | DUoS Amber morning band start, weekday [h] | 7.5 | Verified assumption | National Grid Electricity Distribution West Midlands (MIDE) 2025 Schedule of Charges, Annex 1 time bands. File: MIDE - Schedule of charges and other tables- 2025 V.0.1 for publishing.xlsx | https://commercial.nationalgrid.co.uk/our-network/use-of-system-charges/charging-statements-and-methodology
DUoS Time Band | Midlands |  |  |  | duos_amber_am_end_h | DUoS Amber morning band end, weekday [h] | 16 | Verified assumption | National Grid Electricity Distribution West Midlands (MIDE) 2025 Schedule of Charges, Annex 1 time bands. File: MIDE - Schedule of charges and other tables- 2025 V.0.1 for publishing.xlsx | https://commercial.nationalgrid.co.uk/our-network/use-of-system-charges/charging-statements-and-methodology
DUoS Time Band | Midlands |  |  |  | duos_amber_pm_start_h | DUoS Amber evening band start, weekday [h] | 19 | Verified assumption | National Grid Electricity Distribution West Midlands (MIDE) 2025 Schedule of Charges, Annex 1 time bands. File: MIDE - Schedule of charges and other tables- 2025 V.0.1 for publishing.xlsx | https://commercial.nationalgrid.co.uk/our-network/use-of-system-charges/charging-statements-and-methodology
DUoS Time Band | Midlands |  |  |  | duos_amber_pm_end_h | DUoS Amber evening band end, weekday [h] | 21 | Verified assumption | National Grid Electricity Distribution West Midlands (MIDE) 2025 Schedule of Charges, Annex 1 time bands. File: MIDE - Schedule of charges and other tables- 2025 V.0.1 for publishing.xlsx | https://commercial.nationalgrid.co.uk/our-network/use-of-system-charges/charging-statements-and-methodology
DUoS Time Band | Midlands |  |  |  | duos_we_amber_start_h | DUoS Amber band start, weekend; 0 = none (all Green) [h] | 0 | Verified assumption | National Grid Electricity Distribution West Midlands (MIDE) 2025 Schedule of Charges, Annex 1 time bands. File: MIDE - Schedule of charges and other tables- 2025 V.0.1 for publishing.xlsx | https://commercial.nationalgrid.co.uk/our-network/use-of-system-charges/charging-statements-and-methodology
DUoS Time Band | Midlands |  |  |  | duos_we_amber_end_h | DUoS Amber band end, weekend; 0 = none (all Green) [h] | 0 | Verified assumption | National Grid Electricity Distribution West Midlands (MIDE) 2025 Schedule of Charges, Annex 1 time bands. File: MIDE - Schedule of charges and other tables- 2025 V.0.1 for publishing.xlsx | https://commercial.nationalgrid.co.uk/our-network/use-of-system-charges/charging-statements-and-methodology
DUoS Time Band | Scotland E |  |  |  | duos_red_start_h | DUoS Red band start, weekday [h, 24h decimal] | 16.5 | Verified assumption | SP Distribution (SPD) 2025 Schedule of Charges, Annex 1 time bands. File: SPD-Schedule_of_charges_and_other_tables-2025_V.0.11_Annex6.xlsx | https://www.scottishpower.com/about_us/our_businesses/sp_energy_networks/regulatory_documents/connections_use_of_system_and_metering_services
DUoS Time Band | Scotland E |  |  |  | duos_red_end_h | DUoS Red band end, weekday [h] | 19.5 | Verified assumption | SP Distribution (SPD) 2025 Schedule of Charges, Annex 1 time bands. File: SPD-Schedule_of_charges_and_other_tables-2025_V.0.11_Annex6.xlsx | https://www.scottishpower.com/about_us/our_businesses/sp_energy_networks/regulatory_documents/connections_use_of_system_and_metering_services
DUoS Time Band | Scotland E |  |  |  | duos_amber_am_start_h | DUoS Amber morning band start, weekday [h] | 8 | Verified assumption | SP Distribution (SPD) 2025 Schedule of Charges, Annex 1 time bands. File: SPD-Schedule_of_charges_and_other_tables-2025_V.0.11_Annex6.xlsx | https://www.scottishpower.com/about_us/our_businesses/sp_energy_networks/regulatory_documents/connections_use_of_system_and_metering_services
DUoS Time Band | Scotland E |  |  |  | duos_amber_am_end_h | DUoS Amber morning band end, weekday [h] | 16.5 | Verified assumption | SP Distribution (SPD) 2025 Schedule of Charges, Annex 1 time bands. File: SPD-Schedule_of_charges_and_other_tables-2025_V.0.11_Annex6.xlsx | https://www.scottishpower.com/about_us/our_businesses/sp_energy_networks/regulatory_documents/connections_use_of_system_and_metering_services
DUoS Time Band | Scotland E |  |  |  | duos_amber_pm_start_h | DUoS Amber evening band start, weekday [h] | 19.5 | Verified assumption | SP Distribution (SPD) 2025 Schedule of Charges, Annex 1 time bands. File: SPD-Schedule_of_charges_and_other_tables-2025_V.0.11_Annex6.xlsx | https://www.scottishpower.com/about_us/our_businesses/sp_energy_networks/regulatory_documents/connections_use_of_system_and_metering_services
DUoS Time Band | Scotland E |  |  |  | duos_amber_pm_end_h | DUoS Amber evening band end, weekday [h] | 22.5 | Verified assumption | SP Distribution (SPD) 2025 Schedule of Charges, Annex 1 time bands. File: SPD-Schedule_of_charges_and_other_tables-2025_V.0.11_Annex6.xlsx | https://www.scottishpower.com/about_us/our_businesses/sp_energy_networks/regulatory_documents/connections_use_of_system_and_metering_services
DUoS Time Band | Scotland E |  |  |  | duos_we_amber_start_h | DUoS Amber band start, weekend; 0 = none (all Green) [h] | 16 | Verified assumption | SP Distribution (SPD) 2025 Schedule of Charges, Annex 1 time bands. File: SPD-Schedule_of_charges_and_other_tables-2025_V.0.11_Annex6.xlsx | https://www.scottishpower.com/about_us/our_businesses/sp_energy_networks/regulatory_documents/connections_use_of_system_and_metering_services
DUoS Time Band | Scotland E |  |  |  | duos_we_amber_end_h | DUoS Amber band end, weekend; 0 = none (all Green) [h] | 20 | Verified assumption | SP Distribution (SPD) 2025 Schedule of Charges, Annex 1 time bands. File: SPD-Schedule_of_charges_and_other_tables-2025_V.0.11_Annex6.xlsx | https://www.scottishpower.com/about_us/our_businesses/sp_energy_networks/regulatory_documents/connections_use_of_system_and_metering_services
DUoS Time Band | Scotland N |  |  |  | duos_red_start_h | DUoS Red band start, weekday [h, 24h decimal] | 16 | Verified assumption | SSEN Scottish Hydro Electric Power Distribution (SHEPD) April 2025 Schedule of Charges, Annex 1 time bands. File: shepd---schedule-of-charges-and-other-tables---april-2025-v0.3.xlsx | https://www.ssen.co.uk/about-ssen/library/charging-statements-and-information/scottish-hydro-electric-power-distribution/
DUoS Time Band | Scotland N |  |  |  | duos_red_end_h | DUoS Red band end, weekday [h] | 19 | Verified assumption | SSEN Scottish Hydro Electric Power Distribution (SHEPD) April 2025 Schedule of Charges, Annex 1 time bands. File: shepd---schedule-of-charges-and-other-tables---april-2025-v0.3.xlsx | https://www.ssen.co.uk/about-ssen/library/charging-statements-and-information/scottish-hydro-electric-power-distribution/
DUoS Time Band | Scotland N |  |  |  | duos_amber_am_start_h | DUoS Amber morning band start, weekday [h] | 7 | Verified assumption | SSEN Scottish Hydro Electric Power Distribution (SHEPD) April 2025 Schedule of Charges, Annex 1 time bands. File: shepd---schedule-of-charges-and-other-tables---april-2025-v0.3.xlsx | https://www.ssen.co.uk/about-ssen/library/charging-statements-and-information/scottish-hydro-electric-power-distribution/
DUoS Time Band | Scotland N |  |  |  | duos_amber_am_end_h | DUoS Amber morning band end, weekday [h] | 16 | Verified assumption | SSEN Scottish Hydro Electric Power Distribution (SHEPD) April 2025 Schedule of Charges, Annex 1 time bands. File: shepd---schedule-of-charges-and-other-tables---april-2025-v0.3.xlsx | https://www.ssen.co.uk/about-ssen/library/charging-statements-and-information/scottish-hydro-electric-power-distribution/
DUoS Time Band | Scotland N |  |  |  | duos_amber_pm_start_h | DUoS Amber evening band start, weekday [h] | 19 | Verified assumption | SSEN Scottish Hydro Electric Power Distribution (SHEPD) April 2025 Schedule of Charges, Annex 1 time bands. File: shepd---schedule-of-charges-and-other-tables---april-2025-v0.3.xlsx | https://www.ssen.co.uk/about-ssen/library/charging-statements-and-information/scottish-hydro-electric-power-distribution/
DUoS Time Band | Scotland N |  |  |  | duos_amber_pm_end_h | DUoS Amber evening band end, weekday [h] | 21 | Verified assumption | SSEN Scottish Hydro Electric Power Distribution (SHEPD) April 2025 Schedule of Charges, Annex 1 time bands. File: shepd---schedule-of-charges-and-other-tables---april-2025-v0.3.xlsx | https://www.ssen.co.uk/about-ssen/library/charging-statements-and-information/scottish-hydro-electric-power-distribution/
DUoS Time Band | Scotland N |  |  |  | duos_we_amber_start_h | DUoS Amber band start, weekend; 0 = none (all Green) [h] | 12 | Verified assumption | SSEN Scottish Hydro Electric Power Distribution (SHEPD) April 2025 Schedule of Charges, Annex 1 time bands. File: shepd---schedule-of-charges-and-other-tables---april-2025-v0.3.xlsx | https://www.ssen.co.uk/about-ssen/library/charging-statements-and-information/scottish-hydro-electric-power-distribution/
DUoS Time Band | Scotland N |  |  |  | duos_we_amber_end_h | DUoS Amber band end, weekend; 0 = none (all Green) [h] | 20 | Verified assumption | SSEN Scottish Hydro Electric Power Distribution (SHEPD) April 2025 Schedule of Charges, Annex 1 time bands. File: shepd---schedule-of-charges-and-other-tables---april-2025-v0.3.xlsx | https://www.ssen.co.uk/about-ssen/library/charging-statements-and-information/scottish-hydro-electric-power-distribution/
DUoS Time Band | Scotland W |  |  |  | duos_red_start_h | DUoS Red band start, weekday [h, 24h decimal] | 16.5 | Verified assumption | SP Distribution (SPD) 2025 Schedule of Charges, Annex 1 time bands. File: SPD-Schedule_of_charges_and_other_tables-2025_V.0.11_Annex6.xlsx | https://www.scottishpower.com/about_us/our_businesses/sp_energy_networks/regulatory_documents/connections_use_of_system_and_metering_services
DUoS Time Band | Scotland W |  |  |  | duos_red_end_h | DUoS Red band end, weekday [h] | 19.5 | Verified assumption | SP Distribution (SPD) 2025 Schedule of Charges, Annex 1 time bands. File: SPD-Schedule_of_charges_and_other_tables-2025_V.0.11_Annex6.xlsx | https://www.scottishpower.com/about_us/our_businesses/sp_energy_networks/regulatory_documents/connections_use_of_system_and_metering_services
DUoS Time Band | Scotland W |  |  |  | duos_amber_am_start_h | DUoS Amber morning band start, weekday [h] | 8 | Verified assumption | SP Distribution (SPD) 2025 Schedule of Charges, Annex 1 time bands. File: SPD-Schedule_of_charges_and_other_tables-2025_V.0.11_Annex6.xlsx | https://www.scottishpower.com/about_us/our_businesses/sp_energy_networks/regulatory_documents/connections_use_of_system_and_metering_services
DUoS Time Band | Scotland W |  |  |  | duos_amber_am_end_h | DUoS Amber morning band end, weekday [h] | 16.5 | Verified assumption | SP Distribution (SPD) 2025 Schedule of Charges, Annex 1 time bands. File: SPD-Schedule_of_charges_and_other_tables-2025_V.0.11_Annex6.xlsx | https://www.scottishpower.com/about_us/our_businesses/sp_energy_networks/regulatory_documents/connections_use_of_system_and_metering_services
DUoS Time Band | Scotland W |  |  |  | duos_amber_pm_start_h | DUoS Amber evening band start, weekday [h] | 19.5 | Verified assumption | SP Distribution (SPD) 2025 Schedule of Charges, Annex 1 time bands. File: SPD-Schedule_of_charges_and_other_tables-2025_V.0.11_Annex6.xlsx | https://www.scottishpower.com/about_us/our_businesses/sp_energy_networks/regulatory_documents/connections_use_of_system_and_metering_services
DUoS Time Band | Scotland W |  |  |  | duos_amber_pm_end_h | DUoS Amber evening band end, weekday [h] | 22.5 | Verified assumption | SP Distribution (SPD) 2025 Schedule of Charges, Annex 1 time bands. File: SPD-Schedule_of_charges_and_other_tables-2025_V.0.11_Annex6.xlsx | https://www.scottishpower.com/about_us/our_businesses/sp_energy_networks/regulatory_documents/connections_use_of_system_and_metering_services
DUoS Time Band | Scotland W |  |  |  | duos_we_amber_start_h | DUoS Amber band start, weekend; 0 = none (all Green) [h] | 16 | Verified assumption | SP Distribution (SPD) 2025 Schedule of Charges, Annex 1 time bands. File: SPD-Schedule_of_charges_and_other_tables-2025_V.0.11_Annex6.xlsx | https://www.scottishpower.com/about_us/our_businesses/sp_energy_networks/regulatory_documents/connections_use_of_system_and_metering_services
DUoS Time Band | Scotland W |  |  |  | duos_we_amber_end_h | DUoS Amber band end, weekend; 0 = none (all Green) [h] | 20 | Verified assumption | SP Distribution (SPD) 2025 Schedule of Charges, Annex 1 time bands. File: SPD-Schedule_of_charges_and_other_tables-2025_V.0.11_Annex6.xlsx | https://www.scottishpower.com/about_us/our_businesses/sp_energy_networks/regulatory_documents/connections_use_of_system_and_metering_services
DUoS Unit Charge | East Anglia |  |  |  | duos_red_unit | DUoS Red unit charge, LV HH, A Eastern (UKPN EPN) [GBP/kWh] | 0.08507 | Verified assumption | Eastern Power Networks (UKPN EPN) 2025 Schedule of Charges, Annex 1, 'LV Site Specific' tariff, Red unit charge (p/kWh / 100). File: eastern-power-networks-schedule-of-charges-and-other-tables-2025-v1-9.xlsx | https://www.ukpowernetworks.co.uk/our-company/distribution-use-of-system-charges
DUoS Unit Charge | East Anglia |  |  |  | duos_amber_unit | DUoS Amber unit charge, LV HH, A Eastern (UKPN EPN) [GBP/kWh] | 0.00914 | Verified assumption | Eastern Power Networks (UKPN EPN) 2025 Schedule of Charges, Annex 1, 'LV Site Specific' tariff, Amber unit charge (p/kWh / 100). File: eastern-power-networks-schedule-of-charges-and-other-tables-2025-v1-9.xlsx | https://www.ukpowernetworks.co.uk/our-company/distribution-use-of-system-charges
DUoS Unit Charge | East Anglia |  |  |  | duos_green_unit | DUoS Green unit charge, LV HH, A Eastern (UKPN EPN) [GBP/kWh] | 0.00145 | Verified assumption | Eastern Power Networks (UKPN EPN) 2025 Schedule of Charges, Annex 1, 'LV Site Specific' tariff, Green unit charge (p/kWh / 100). File: eastern-power-networks-schedule-of-charges-and-other-tables-2025-v1-9.xlsx | https://www.ukpowernetworks.co.uk/our-company/distribution-use-of-system-charges
DUoS Unit Charge | England E and NE |  |  |  | duos_red_unit | DUoS Red unit charge, LV HH, F North East (Northern Powergrid) [GBP/kWh] | 0.07118 | Verified assumption | Northern Powergrid Northeast 2025-26 Schedule of Charges, Annex 1, 'LV Site Specific' tariff, Red unit charge (p/kWh / 100). File: Northern Powergrid (Northeast) - 2025-26 Schedule of charges and other tables v0.2.xlsx | https://www.northernpowergrid.com/node/1526
DUoS Unit Charge | England E and NE |  |  |  | duos_amber_unit | DUoS Amber unit charge, LV HH, F North East (Northern Powergrid) [GBP/kWh] | 0.01153 | Verified assumption | Northern Powergrid Northeast 2025-26 Schedule of Charges, Annex 1, 'LV Site Specific' tariff, Amber unit charge (p/kWh / 100). File: Northern Powergrid (Northeast) - 2025-26 Schedule of charges and other tables v0.2.xlsx | https://www.northernpowergrid.com/node/1526
DUoS Unit Charge | England E and NE |  |  |  | duos_green_unit | DUoS Green unit charge, LV HH, F North East (Northern Powergrid) [GBP/kWh] | 0.00222 | Verified assumption | Northern Powergrid Northeast 2025-26 Schedule of Charges, Annex 1, 'LV Site Specific' tariff, Green unit charge (p/kWh / 100). File: Northern Powergrid (Northeast) - 2025-26 Schedule of charges and other tables v0.2.xlsx | https://www.northernpowergrid.com/node/1526
DUoS Unit Charge | England NW and N Wales |  |  |  | duos_red_unit | DUoS Red unit charge, LV HH, G North West (Electricity North West) [GBP/kWh] | 0.10792 | Verified assumption | Electricity North West (ENWL) 2025 Schedule of Charges, Annex 1, 'LV Site Specific' tariff, Red unit charge (p/kWh / 100). File: enwl---schedule-of-charges-and-other-tables--2025-v2_0.xlsx | https://www.enwl.co.uk/about-us/regulatory-information/use-of-system-charges/current-charging-information/
DUoS Unit Charge | England NW and N Wales |  |  |  | duos_amber_unit | DUoS Amber unit charge, LV HH, G North West (Electricity North West) [GBP/kWh] | 0.01788 | Verified assumption | Electricity North West (ENWL) 2025 Schedule of Charges, Annex 1, 'LV Site Specific' tariff, Amber unit charge (p/kWh / 100). File: enwl---schedule-of-charges-and-other-tables--2025-v2_0.xlsx | https://www.enwl.co.uk/about-us/regulatory-information/use-of-system-charges/current-charging-information/
DUoS Unit Charge | England NW and N Wales |  |  |  | duos_green_unit | DUoS Green unit charge, LV HH, G North West (Electricity North West) [GBP/kWh] | 0.00081 | Verified assumption | Electricity North West (ENWL) 2025 Schedule of Charges, Annex 1, 'LV Site Specific' tariff, Green unit charge (p/kWh / 100). File: enwl---schedule-of-charges-and-other-tables--2025-v2_0.xlsx | https://www.enwl.co.uk/about-us/regulatory-information/use-of-system-charges/current-charging-information/
DUoS Unit Charge | England SE and Central S |  |  |  | duos_red_unit | DUoS Red unit charge, LV HH, H Southern (SSEN SEPD) [GBP/kWh] | 0.07623 | Verified assumption | SSEN Southern (SEPD) 2025 Schedule of Charges, Annex 1, 'LV Site Specific No Residual' tariff, Red unit charge (p/kWh / 100). File: sepd---schedule-of-charges-and-other-tables---april-2025-v0.3.xlsx | https://www.ssen.co.uk/about-ssen/library/charging-statements-and-information/southern-electric-power-distribution/
DUoS Unit Charge | England SE and Central S |  |  |  | duos_amber_unit | DUoS Amber unit charge, LV HH, H Southern (SSEN SEPD) [GBP/kWh] | 0.00878 | Verified assumption | SSEN Southern (SEPD) 2025 Schedule of Charges, Annex 1, 'LV Site Specific No Residual' tariff, Amber unit charge (p/kWh / 100). File: sepd---schedule-of-charges-and-other-tables---april-2025-v0.3.xlsx | https://www.ssen.co.uk/about-ssen/library/charging-statements-and-information/southern-electric-power-distribution/
DUoS Unit Charge | England SE and Central S |  |  |  | duos_green_unit | DUoS Green unit charge, LV HH, H Southern (SSEN SEPD) [GBP/kWh] | 0.00043 | Verified assumption | SSEN Southern (SEPD) 2025 Schedule of Charges, Annex 1, 'LV Site Specific No Residual' tariff, Green unit charge (p/kWh / 100). File: sepd---schedule-of-charges-and-other-tables---april-2025-v0.3.xlsx | https://www.ssen.co.uk/about-ssen/library/charging-statements-and-information/southern-electric-power-distribution/
DUoS Unit Charge | England SW and S Wales |  |  |  | duos_red_unit | DUoS Red unit charge, LV HH, L South West (NGED South West) [GBP/kWh] | 0.15821 | Verified assumption | NGED South West (SWEB) 2025 Schedule of Charges, Annex 1, 'LV Site Specific' tariff, Red unit charge (p/kWh / 100). File: SWEB - Schedule of charges and other tables- 2025 V.0.1 for publishing.xlsx | https://commercial.nationalgrid.co.uk/our-network/use-of-system-charges/charging-statements-and-methodology
DUoS Unit Charge | England SW and S Wales |  |  |  | duos_amber_unit | DUoS Amber unit charge, LV HH, L South West (NGED South West) [GBP/kWh] | 0.00944 | Verified assumption | NGED South West (SWEB) 2025 Schedule of Charges, Annex 1, 'LV Site Specific' tariff, Amber unit charge (p/kWh / 100). File: SWEB - Schedule of charges and other tables- 2025 V.0.1 for publishing.xlsx | https://commercial.nationalgrid.co.uk/our-network/use-of-system-charges/charging-statements-and-methodology
DUoS Unit Charge | England SW and S Wales |  |  |  | duos_green_unit | DUoS Green unit charge, LV HH, L South West (NGED South West) [GBP/kWh] | 0.00114 | Verified assumption | NGED South West (SWEB) 2025 Schedule of Charges, Annex 1, 'LV Site Specific' tariff, Green unit charge (p/kWh / 100). File: SWEB - Schedule of charges and other tables- 2025 V.0.1 for publishing.xlsx | https://commercial.nationalgrid.co.uk/our-network/use-of-system-charges/charging-statements-and-methodology
DUoS Unit Charge | Midlands |  |  |  | duos_red_unit | DUoS Red unit charge, LV HH, E West Midlands (NGED West Midlands) [GBP/kWh] | 0.05967 | Verified assumption | NGED West Midlands (MIDE) 2025 Schedule of Charges, Annex 1, 'LV Site Specific' tariff, Red unit charge (p/kWh / 100). File: MIDE - Schedule of charges and other tables- 2025 V.0.1 for publishing.xlsx | https://commercial.nationalgrid.co.uk/our-network/use-of-system-charges/charging-statements-and-methodology
DUoS Unit Charge | Midlands |  |  |  | duos_amber_unit | DUoS Amber unit charge, LV HH, E West Midlands (NGED West Midlands) [GBP/kWh] | 0.00967 | Verified assumption | NGED West Midlands (MIDE) 2025 Schedule of Charges, Annex 1, 'LV Site Specific' tariff, Amber unit charge (p/kWh / 100). File: MIDE - Schedule of charges and other tables- 2025 V.0.1 for publishing.xlsx | https://commercial.nationalgrid.co.uk/our-network/use-of-system-charges/charging-statements-and-methodology
DUoS Unit Charge | Midlands |  |  |  | duos_green_unit | DUoS Green unit charge, LV HH, E West Midlands (NGED West Midlands) [GBP/kWh] | 0.00133 | Verified assumption | NGED West Midlands (MIDE) 2025 Schedule of Charges, Annex 1, 'LV Site Specific' tariff, Green unit charge (p/kWh / 100). File: MIDE - Schedule of charges and other tables- 2025 V.0.1 for publishing.xlsx | https://commercial.nationalgrid.co.uk/our-network/use-of-system-charges/charging-statements-and-methodology
DUoS Unit Charge | Scotland E |  |  |  | duos_red_unit | DUoS Red unit charge, LV HH, N S Scotland (SP Distribution) [GBP/kWh] | 0.1005 | Verified assumption | SP Distribution (SPD) 2025 Schedule of Charges, Annex 1, 'LV Site Specific' tariff, Red unit charge (p/kWh / 100). File: SPD-Schedule_of_charges_and_other_tables-2025_V.0.11_Annex6.xlsx | https://www.scottishpower.com/about_us/our_businesses/sp_energy_networks/regulatory_documents/connections_use_of_system_and_metering_services
DUoS Unit Charge | Scotland E |  |  |  | duos_amber_unit | DUoS Amber unit charge, LV HH, N S Scotland (SP Distribution) [GBP/kWh] | 0.01029 | Verified assumption | SP Distribution (SPD) 2025 Schedule of Charges, Annex 1, 'LV Site Specific' tariff, Amber unit charge (p/kWh / 100). File: SPD-Schedule_of_charges_and_other_tables-2025_V.0.11_Annex6.xlsx | https://www.scottishpower.com/about_us/our_businesses/sp_energy_networks/regulatory_documents/connections_use_of_system_and_metering_services
DUoS Unit Charge | Scotland E |  |  |  | duos_green_unit | DUoS Green unit charge, LV HH, N S Scotland (SP Distribution) [GBP/kWh] | 0.00021 | Verified assumption | SP Distribution (SPD) 2025 Schedule of Charges, Annex 1, 'LV Site Specific' tariff, Green unit charge (p/kWh / 100). File: SPD-Schedule_of_charges_and_other_tables-2025_V.0.11_Annex6.xlsx | https://www.scottishpower.com/about_us/our_businesses/sp_energy_networks/regulatory_documents/connections_use_of_system_and_metering_services
DUoS Unit Charge | Scotland N |  |  |  | duos_red_unit | DUoS Red unit charge, LV HH, P N Scotland (SSEN SHEPD) [GBP/kWh] | 0.07901 | Verified assumption | SSEN North Scotland (SHEPD) 2025 Schedule of Charges, Annex 1, 'LV Site Specific' tariff, Red unit charge (p/kWh / 100). File: shepd---schedule-of-charges-and-other-tables---april-2025-v0.3.xlsx | https://www.ssen.co.uk/about-ssen/library/charging-statements-and-information/southern-electric-power-distribution/
DUoS Unit Charge | Scotland N |  |  |  | duos_amber_unit | DUoS Amber unit charge, LV HH, P N Scotland (SSEN SHEPD) [GBP/kWh] | 0.02684 | Verified assumption | SSEN North Scotland (SHEPD) 2025 Schedule of Charges, Annex 1, 'LV Site Specific' tariff, Amber unit charge (p/kWh / 100). File: shepd---schedule-of-charges-and-other-tables---april-2025-v0.3.xlsx | https://www.ssen.co.uk/about-ssen/library/charging-statements-and-information/southern-electric-power-distribution/
DUoS Unit Charge | Scotland N |  |  |  | duos_green_unit | DUoS Green unit charge, LV HH, P N Scotland (SSEN SHEPD) [GBP/kWh] | 0.00599 | Verified assumption | SSEN North Scotland (SHEPD) 2025 Schedule of Charges, Annex 1, 'LV Site Specific' tariff, Green unit charge (p/kWh / 100). File: shepd---schedule-of-charges-and-other-tables---april-2025-v0.3.xlsx | https://www.ssen.co.uk/about-ssen/library/charging-statements-and-information/southern-electric-power-distribution/
DUoS Unit Charge | Scotland W |  |  |  | duos_red_unit | DUoS Red unit charge, LV HH, N S Scotland (SP Distribution) [GBP/kWh] | 0.1005 | Verified assumption | SP Distribution (SPD) 2025 Schedule of Charges, Annex 1, 'LV Site Specific' tariff, Red unit charge (p/kWh / 100). File: SPD-Schedule_of_charges_and_other_tables-2025_V.0.11_Annex6.xlsx | https://www.spenergynetworks.co.uk/pages/connections_use_of_system_and_metering_services.aspx
DUoS Unit Charge | Scotland W |  |  |  | duos_amber_unit | DUoS Amber unit charge, LV HH, N S Scotland (SP Distribution) [GBP/kWh] | 0.01029 | Verified assumption | SP Distribution (SPD) 2025 Schedule of Charges, Annex 1, 'LV Site Specific' tariff, Amber unit charge (p/kWh / 100). File: SPD-Schedule_of_charges_and_other_tables-2025_V.0.11_Annex6.xlsx | https://www.spenergynetworks.co.uk/pages/connections_use_of_system_and_metering_services.aspx
DUoS Unit Charge | Scotland W |  |  |  | duos_green_unit | DUoS Green unit charge, LV HH, N S Scotland (SP Distribution) [GBP/kWh] | 0.00021 | Verified assumption | SP Distribution (SPD) 2025 Schedule of Charges, Annex 1, 'LV Site Specific' tariff, Green unit charge (p/kWh / 100). File: SPD-Schedule_of_charges_and_other_tables-2025_V.0.11_Annex6.xlsx | https://www.spenergynetworks.co.uk/pages/connections_use_of_system_and_metering_services.aspx
Retail Non-Commodity | Very Small |  |  |  | non_commodity_other | Residual non-commodity adder, Very Small band [GBP/kWh, real 2025] | 0.24531 | Verified assumption | Band-specific residual non-commodity adder (TNUoS+BSUoS+RO/CfD/FiT+Capacity Market+supplier margin). Reconciled per DESNZ electricity import band: residual = delivered_band_price - wholesale_avg(0.08249, Elexon MID 2025) - national_DUoS_avg(0.01336, day-weighted R/A/G blend averaged over districts) - CCL(0.00801). With calibration OFF, regional DUoS then differentiates each district mean around the GB delivered price. Re-derive when DUoS rates change. | https://www.gov.uk/government/statistical-data-sets/gas-and-electricity-prices-in-the-non-domestic-sector
Retail Non-Commodity | Small |  |  |  | non_commodity_other | Residual non-commodity adder, Small band [GBP/kWh, real 2025] | 0.18695 | Verified assumption | Band-specific residual non-commodity adder (TNUoS+BSUoS+RO/CfD/FiT+Capacity Market+supplier margin). Reconciled per DESNZ electricity import band: residual = delivered_band_price - wholesale_avg(0.08249, Elexon MID 2025) - national_DUoS_avg(0.01336, day-weighted R/A/G blend averaged over districts) - CCL(0.00801). With calibration OFF, regional DUoS then differentiates each district mean around the GB delivered price. Re-derive when DUoS rates change. | https://www.gov.uk/government/statistical-data-sets/gas-and-electricity-prices-in-the-non-domestic-sector
Retail Non-Commodity | Small/Medium |  |  |  | non_commodity_other | Residual non-commodity adder, Small/Medium band [GBP/kWh, real 2025] | 0.17848 | Verified assumption | Band-specific residual non-commodity adder (TNUoS+BSUoS+RO/CfD/FiT+Capacity Market+supplier margin). Reconciled per DESNZ electricity import band: residual = delivered_band_price - wholesale_avg(0.08249, Elexon MID 2025) - national_DUoS_avg(0.01336, day-weighted R/A/G blend averaged over districts) - CCL(0.00801). With calibration OFF, regional DUoS then differentiates each district mean around the GB delivered price. Re-derive when DUoS rates change. | https://www.gov.uk/government/statistical-data-sets/gas-and-electricity-prices-in-the-non-domestic-sector
Retail Non-Commodity | Medium |  |  |  | non_commodity_other | Residual non-commodity adder, Medium band [GBP/kWh, real 2025] | 0.15507 | Verified assumption | Band-specific residual non-commodity adder (TNUoS+BSUoS+RO/CfD/FiT+Capacity Market+supplier margin). Reconciled per DESNZ electricity import band: residual = delivered_band_price - wholesale_avg(0.08249, Elexon MID 2025) - national_DUoS_avg(0.01336, day-weighted R/A/G blend averaged over districts) - CCL(0.00801). With calibration OFF, regional DUoS then differentiates each district mean around the GB delivered price. Re-derive when DUoS rates change. | https://www.gov.uk/government/statistical-data-sets/gas-and-electricity-prices-in-the-non-domestic-sector
Retail Non-Commodity | Large |  |  |  | non_commodity_other | Residual non-commodity adder, Large band [GBP/kWh, real 2025] | 0.14003 | Verified assumption | Band-specific residual non-commodity adder (TNUoS+BSUoS+RO/CfD/FiT+Capacity Market+supplier margin). Reconciled per DESNZ electricity import band: residual = delivered_band_price - wholesale_avg(0.08249, Elexon MID 2025) - national_DUoS_avg(0.01336, day-weighted R/A/G blend averaged over districts) - CCL(0.00801). With calibration OFF, regional DUoS then differentiates each district mean around the GB delivered price. Re-derive when DUoS rates change. | https://www.gov.uk/government/statistical-data-sets/gas-and-electricity-prices-in-the-non-domestic-sector
Retail Non-Commodity | Very Large |  |  |  | non_commodity_other | Residual non-commodity adder, Very Large band [GBP/kWh, real 2025] | 0.11697 | Verified assumption | Band-specific residual non-commodity adder (TNUoS+BSUoS+RO/CfD/FiT+Capacity Market+supplier margin). Reconciled per DESNZ electricity import band: residual = delivered_band_price - wholesale_avg(0.08249, Elexon MID 2025) - national_DUoS_avg(0.01336, day-weighted R/A/G blend averaged over districts) - CCL(0.00801). With calibration OFF, regional DUoS then differentiates each district mean around the GB delivered price. Re-derive when DUoS rates change. | https://www.gov.uk/government/statistical-data-sets/gas-and-electricity-prices-in-the-non-domestic-sector
Retail Non-Commodity | Extra Large |  |  |  | non_commodity_other | Residual non-commodity adder, Extra Large band [GBP/kWh, real 2025] | 0.10981 | Verified assumption | Band-specific residual non-commodity adder (TNUoS+BSUoS+RO/CfD/FiT+Capacity Market+supplier margin). Reconciled per DESNZ electricity import band: residual = delivered_band_price - wholesale_avg(0.08249, Elexon MID 2025) - national_DUoS_avg(0.01336, day-weighted R/A/G blend averaged over districts) - CCL(0.00801). With calibration OFF, regional DUoS then differentiates each district mean around the GB delivered price. Re-derive when DUoS rates change. | https://www.gov.uk/government/statistical-data-sets/gas-and-electricity-prices-in-the-non-domestic-sector

## Emissions
Group | Scenario | Year | Active | Parameter | Description (units) | Value | Type | Source | Source URL | Price Base Year
Gas Emission Factor |  |  |  | gas_emission_factor | Natural gas combustion emission factor [kgCO2e/kWh, gross CV] | 0.18293 | Verified assumption | DESNZ supplementary guidance: data tables data-tables-1-19.xlsx (updated 17 Apr 2023), Table 2a (Converting fuel types to CO2 and CO2e (emissions factors)) — Natural Gas, 'All GHG emissions (kgCO2e per unit) (AR5)', kWh (gross CV). | https://www.gov.uk/government/publications/valuation-of-energy-use-and-greenhouse-gas-emissions-for-appraisal
Electricity Emission Factor |  | 2025 |  | elec_emission_factor | Grid electricity emission factor 2025 [kgCO2e/kWh, LRM consumption-based, Commercial/Public] | 0.20719 | Verified assumption | DESNZ supplementary guidance: data tables data-tables-1-19.xlsx (updated 17 Apr 2023), Table 1 (Electricity emissions factors to 2100, kgCO2e/kWh) — 'Long-run marginal' / 'Consumption-based' / 'Commercial/ Public sector' column. Consumption-based includes transmission and distribution losses; long-run marginal is the basis the table specifies for measuring small changes in consumption (grid average is for footprinting only). Trajectory reflects the decarbonising grid. | https://www.gov.uk/government/publications/valuation-of-energy-use-and-greenhouse-gas-emissions-for-appraisal
Electricity Emission Factor |  | 2026 |  | elec_emission_factor | Grid electricity emission factor 2026 [kgCO2e/kWh, LRM consumption-based, Commercial/Public] | 0.18723 | Verified assumption | DESNZ supplementary guidance: data tables data-tables-1-19.xlsx (updated 17 Apr 2023), Table 1 (Electricity emissions factors to 2100, kgCO2e/kWh) — 'Long-run marginal' / 'Consumption-based' / 'Commercial/ Public sector' column. Consumption-based includes transmission and distribution losses; long-run marginal is the basis the table specifies for measuring small changes in consumption (grid average is for footprinting only). Trajectory reflects the decarbonising grid. | https://www.gov.uk/government/publications/valuation-of-energy-use-and-greenhouse-gas-emissions-for-appraisal
Electricity Emission Factor |  | 2027 |  | elec_emission_factor | Grid electricity emission factor 2027 [kgCO2e/kWh, LRM consumption-based, Commercial/Public] | 0.16578 | Verified assumption | DESNZ supplementary guidance: data tables data-tables-1-19.xlsx (updated 17 Apr 2023), Table 1 (Electricity emissions factors to 2100, kgCO2e/kWh) — 'Long-run marginal' / 'Consumption-based' / 'Commercial/ Public sector' column. Consumption-based includes transmission and distribution losses; long-run marginal is the basis the table specifies for measuring small changes in consumption (grid average is for footprinting only). Trajectory reflects the decarbonising grid. | https://www.gov.uk/government/publications/valuation-of-energy-use-and-greenhouse-gas-emissions-for-appraisal
Electricity Emission Factor |  | 2028 |  | elec_emission_factor | Grid electricity emission factor 2028 [kgCO2e/kWh, LRM consumption-based, Commercial/Public] | 0.14274 | Verified assumption | DESNZ supplementary guidance: data tables data-tables-1-19.xlsx (updated 17 Apr 2023), Table 1 (Electricity emissions factors to 2100, kgCO2e/kWh) — 'Long-run marginal' / 'Consumption-based' / 'Commercial/ Public sector' column. Consumption-based includes transmission and distribution losses; long-run marginal is the basis the table specifies for measuring small changes in consumption (grid average is for footprinting only). Trajectory reflects the decarbonising grid. | https://www.gov.uk/government/publications/valuation-of-energy-use-and-greenhouse-gas-emissions-for-appraisal
Electricity Emission Factor |  | 2029 |  | elec_emission_factor | Grid electricity emission factor 2029 [kgCO2e/kWh, LRM consumption-based, Commercial/Public] | 0.11799 | Verified assumption | DESNZ supplementary guidance: data tables data-tables-1-19.xlsx (updated 17 Apr 2023), Table 1 (Electricity emissions factors to 2100, kgCO2e/kWh) — 'Long-run marginal' / 'Consumption-based' / 'Commercial/ Public sector' column. Consumption-based includes transmission and distribution losses; long-run marginal is the basis the table specifies for measuring small changes in consumption (grid average is for footprinting only). Trajectory reflects the decarbonising grid. | https://www.gov.uk/government/publications/valuation-of-energy-use-and-greenhouse-gas-emissions-for-appraisal
Electricity Emission Factor |  | 2030 |  | elec_emission_factor | Grid electricity emission factor 2030 [kgCO2e/kWh, LRM consumption-based, Commercial/Public] | 0.091393 | Verified assumption | DESNZ supplementary guidance: data tables data-tables-1-19.xlsx (updated 17 Apr 2023), Table 1 (Electricity emissions factors to 2100, kgCO2e/kWh) — 'Long-run marginal' / 'Consumption-based' / 'Commercial/ Public sector' column. Consumption-based includes transmission and distribution losses; long-run marginal is the basis the table specifies for measuring small changes in consumption (grid average is for footprinting only). Trajectory reflects the decarbonising grid. | https://www.gov.uk/government/publications/valuation-of-energy-use-and-greenhouse-gas-emissions-for-appraisal
Electricity Emission Factor |  | 2031 |  | elec_emission_factor | Grid electricity emission factor 2031 [kgCO2e/kWh, LRM consumption-based, Commercial/Public] | 0.07014 | Verified assumption | DESNZ supplementary guidance: data tables data-tables-1-19.xlsx (updated 17 Apr 2023), Table 1 (Electricity emissions factors to 2100, kgCO2e/kWh) — 'Long-run marginal' / 'Consumption-based' / 'Commercial/ Public sector' column. Consumption-based includes transmission and distribution losses; long-run marginal is the basis the table specifies for measuring small changes in consumption (grid average is for footprinting only). Trajectory reflects the decarbonising grid. | https://www.gov.uk/government/publications/valuation-of-energy-use-and-greenhouse-gas-emissions-for-appraisal
Electricity Emission Factor |  | 2032 |  | elec_emission_factor | Grid electricity emission factor 2032 [kgCO2e/kWh, LRM consumption-based, Commercial/Public] | 0.053829 | Verified assumption | DESNZ supplementary guidance: data tables data-tables-1-19.xlsx (updated 17 Apr 2023), Table 1 (Electricity emissions factors to 2100, kgCO2e/kWh) — 'Long-run marginal' / 'Consumption-based' / 'Commercial/ Public sector' column. Consumption-based includes transmission and distribution losses; long-run marginal is the basis the table specifies for measuring small changes in consumption (grid average is for footprinting only). Trajectory reflects the decarbonising grid. | https://www.gov.uk/government/publications/valuation-of-energy-use-and-greenhouse-gas-emissions-for-appraisal
Electricity Emission Factor |  | 2033 |  | elec_emission_factor | Grid electricity emission factor 2033 [kgCO2e/kWh, LRM consumption-based, Commercial/Public] | 0.041311 | Verified assumption | DESNZ supplementary guidance: data tables data-tables-1-19.xlsx (updated 17 Apr 2023), Table 1 (Electricity emissions factors to 2100, kgCO2e/kWh) — 'Long-run marginal' / 'Consumption-based' / 'Commercial/ Public sector' column. Consumption-based includes transmission and distribution losses; long-run marginal is the basis the table specifies for measuring small changes in consumption (grid average is for footprinting only). Trajectory reflects the decarbonising grid. | https://www.gov.uk/government/publications/valuation-of-energy-use-and-greenhouse-gas-emissions-for-appraisal
Electricity Emission Factor |  | 2034 |  | elec_emission_factor | Grid electricity emission factor 2034 [kgCO2e/kWh, LRM consumption-based, Commercial/Public] | 0.031705 | Verified assumption | DESNZ supplementary guidance: data tables data-tables-1-19.xlsx (updated 17 Apr 2023), Table 1 (Electricity emissions factors to 2100, kgCO2e/kWh) — 'Long-run marginal' / 'Consumption-based' / 'Commercial/ Public sector' column. Consumption-based includes transmission and distribution losses; long-run marginal is the basis the table specifies for measuring small changes in consumption (grid average is for footprinting only). Trajectory reflects the decarbonising grid. | https://www.gov.uk/government/publications/valuation-of-energy-use-and-greenhouse-gas-emissions-for-appraisal
Electricity Emission Factor |  | 2035 |  | elec_emission_factor | Grid electricity emission factor 2035 [kgCO2e/kWh, LRM consumption-based, Commercial/Public] | 0.024332 | Verified assumption | DESNZ supplementary guidance: data tables data-tables-1-19.xlsx (updated 17 Apr 2023), Table 1 (Electricity emissions factors to 2100, kgCO2e/kWh) — 'Long-run marginal' / 'Consumption-based' / 'Commercial/ Public sector' column. Consumption-based includes transmission and distribution losses; long-run marginal is the basis the table specifies for measuring small changes in consumption (grid average is for footprinting only). Trajectory reflects the decarbonising grid. | https://www.gov.uk/government/publications/valuation-of-energy-use-and-greenhouse-gas-emissions-for-appraisal
Electricity Emission Factor |  | 2036 |  | elec_emission_factor | Grid electricity emission factor 2036 [kgCO2e/kWh, LRM consumption-based, Commercial/Public] | 0.018674 | Verified assumption | DESNZ supplementary guidance: data tables data-tables-1-19.xlsx (updated 17 Apr 2023), Table 1 (Electricity emissions factors to 2100, kgCO2e/kWh) — 'Long-run marginal' / 'Consumption-based' / 'Commercial/ Public sector' column. Consumption-based includes transmission and distribution losses; long-run marginal is the basis the table specifies for measuring small changes in consumption (grid average is for footprinting only). Trajectory reflects the decarbonising grid. | https://www.gov.uk/government/publications/valuation-of-energy-use-and-greenhouse-gas-emissions-for-appraisal
Electricity Emission Factor |  | 2037 |  | elec_emission_factor | Grid electricity emission factor 2037 [kgCO2e/kWh, LRM consumption-based, Commercial/Public] | 0.014331 | Verified assumption | DESNZ supplementary guidance: data tables data-tables-1-19.xlsx (updated 17 Apr 2023), Table 1 (Electricity emissions factors to 2100, kgCO2e/kWh) — 'Long-run marginal' / 'Consumption-based' / 'Commercial/ Public sector' column. Consumption-based includes transmission and distribution losses; long-run marginal is the basis the table specifies for measuring small changes in consumption (grid average is for footprinting only). Trajectory reflects the decarbonising grid. | https://www.gov.uk/government/publications/valuation-of-energy-use-and-greenhouse-gas-emissions-for-appraisal
Electricity Emission Factor |  | 2038 |  | elec_emission_factor | Grid electricity emission factor 2038 [kgCO2e/kWh, LRM consumption-based, Commercial/Public] | 0.010999 | Verified assumption | DESNZ supplementary guidance: data tables data-tables-1-19.xlsx (updated 17 Apr 2023), Table 1 (Electricity emissions factors to 2100, kgCO2e/kWh) — 'Long-run marginal' / 'Consumption-based' / 'Commercial/ Public sector' column. Consumption-based includes transmission and distribution losses; long-run marginal is the basis the table specifies for measuring small changes in consumption (grid average is for footprinting only). Trajectory reflects the decarbonising grid. | https://www.gov.uk/government/publications/valuation-of-energy-use-and-greenhouse-gas-emissions-for-appraisal
Electricity Emission Factor |  | 2039 |  | elec_emission_factor | Grid electricity emission factor 2039 [kgCO2e/kWh, LRM consumption-based, Commercial/Public] | 0.008441 | Verified assumption | DESNZ supplementary guidance: data tables data-tables-1-19.xlsx (updated 17 Apr 2023), Table 1 (Electricity emissions factors to 2100, kgCO2e/kWh) — 'Long-run marginal' / 'Consumption-based' / 'Commercial/ Public sector' column. Consumption-based includes transmission and distribution losses; long-run marginal is the basis the table specifies for measuring small changes in consumption (grid average is for footprinting only). Trajectory reflects the decarbonising grid. | https://www.gov.uk/government/publications/valuation-of-energy-use-and-greenhouse-gas-emissions-for-appraisal
Carbon Value | Central | 2025 | yes | carbon_value | Appraisal carbon value 2025 [GBP(2022)/tCO2e, Central] | 273.06 | Verified assumption | DESNZ supplementary guidance: data tables data-tables-1-19.xlsx (updated 17 Apr 2023), Table 3 (Carbon values and sensitivities 2010-2100 for appraisal, 2022 GBP/tCO2e) — Central column. Low/High sensitivities are published as their own columns and equal Central x0.5 / x1.5 (DESNZ +-50% range); only the Central series is transcribed, selected via the Scenario/Active columns. | https://www.gov.uk/government/publications/valuation-of-energy-use-and-greenhouse-gas-emissions-for-appraisal | 2022
Carbon Value | Central | 2026 | yes | carbon_value | Appraisal carbon value 2026 [GBP(2022)/tCO2e, Central] | 277.22 | Verified assumption | DESNZ supplementary guidance: data tables data-tables-1-19.xlsx (updated 17 Apr 2023), Table 3 (Carbon values and sensitivities 2010-2100 for appraisal, 2022 GBP/tCO2e) — Central column. Low/High sensitivities are published as their own columns and equal Central x0.5 / x1.5 (DESNZ +-50% range); only the Central series is transcribed, selected via the Scenario/Active columns. | https://www.gov.uk/government/publications/valuation-of-energy-use-and-greenhouse-gas-emissions-for-appraisal | 2022
Carbon Value | Central | 2027 | yes | carbon_value | Appraisal carbon value 2027 [GBP(2022)/tCO2e, Central] | 281.44 | Verified assumption | DESNZ supplementary guidance: data tables data-tables-1-19.xlsx (updated 17 Apr 2023), Table 3 (Carbon values and sensitivities 2010-2100 for appraisal, 2022 GBP/tCO2e) — Central column. Low/High sensitivities are published as their own columns and equal Central x0.5 / x1.5 (DESNZ +-50% range); only the Central series is transcribed, selected via the Scenario/Active columns. | https://www.gov.uk/government/publications/valuation-of-energy-use-and-greenhouse-gas-emissions-for-appraisal | 2022
Carbon Value | Central | 2028 | yes | carbon_value | Appraisal carbon value 2028 [GBP(2022)/tCO2e, Central] | 285.73 | Verified assumption | DESNZ supplementary guidance: data tables data-tables-1-19.xlsx (updated 17 Apr 2023), Table 3 (Carbon values and sensitivities 2010-2100 for appraisal, 2022 GBP/tCO2e) — Central column. Low/High sensitivities are published as their own columns and equal Central x0.5 / x1.5 (DESNZ +-50% range); only the Central series is transcribed, selected via the Scenario/Active columns. | https://www.gov.uk/government/publications/valuation-of-energy-use-and-greenhouse-gas-emissions-for-appraisal | 2022
Carbon Value | Central | 2029 | yes | carbon_value | Appraisal carbon value 2029 [GBP(2022)/tCO2e, Central] | 290.08 | Verified assumption | DESNZ supplementary guidance: data tables data-tables-1-19.xlsx (updated 17 Apr 2023), Table 3 (Carbon values and sensitivities 2010-2100 for appraisal, 2022 GBP/tCO2e) — Central column. Low/High sensitivities are published as their own columns and equal Central x0.5 / x1.5 (DESNZ +-50% range); only the Central series is transcribed, selected via the Scenario/Active columns. | https://www.gov.uk/government/publications/valuation-of-energy-use-and-greenhouse-gas-emissions-for-appraisal | 2022
Carbon Value | Central | 2030 | yes | carbon_value | Appraisal carbon value 2030 [GBP(2022)/tCO2e, Central] | 294.5 | Verified assumption | DESNZ supplementary guidance: data tables data-tables-1-19.xlsx (updated 17 Apr 2023), Table 3 (Carbon values and sensitivities 2010-2100 for appraisal, 2022 GBP/tCO2e) — Central column. Low/High sensitivities are published as their own columns and equal Central x0.5 / x1.5 (DESNZ +-50% range); only the Central series is transcribed, selected via the Scenario/Active columns. | https://www.gov.uk/government/publications/valuation-of-energy-use-and-greenhouse-gas-emissions-for-appraisal | 2022
Carbon Value | Central | 2031 | yes | carbon_value | Appraisal carbon value 2031 [GBP(2022)/tCO2e, Central] | 298.98 | Verified assumption | DESNZ supplementary guidance: data tables data-tables-1-19.xlsx (updated 17 Apr 2023), Table 3 (Carbon values and sensitivities 2010-2100 for appraisal, 2022 GBP/tCO2e) — Central column. Low/High sensitivities are published as their own columns and equal Central x0.5 / x1.5 (DESNZ +-50% range); only the Central series is transcribed, selected via the Scenario/Active columns. | https://www.gov.uk/government/publications/valuation-of-energy-use-and-greenhouse-gas-emissions-for-appraisal | 2022
Carbon Value | Central | 2032 | yes | carbon_value | Appraisal carbon value 2032 [GBP(2022)/tCO2e, Central] | 303.54 | Verified assumption | DESNZ supplementary guidance: data tables data-tables-1-19.xlsx (updated 17 Apr 2023), Table 3 (Carbon values and sensitivities 2010-2100 for appraisal, 2022 GBP/tCO2e) — Central column. Low/High sensitivities are published as their own columns and equal Central x0.5 / x1.5 (DESNZ +-50% range); only the Central series is transcribed, selected via the Scenario/Active columns. | https://www.gov.uk/government/publications/valuation-of-energy-use-and-greenhouse-gas-emissions-for-appraisal | 2022
Carbon Value | Central | 2033 | yes | carbon_value | Appraisal carbon value 2033 [GBP(2022)/tCO2e, Central] | 308.16 | Verified assumption | DESNZ supplementary guidance: data tables data-tables-1-19.xlsx (updated 17 Apr 2023), Table 3 (Carbon values and sensitivities 2010-2100 for appraisal, 2022 GBP/tCO2e) — Central column. Low/High sensitivities are published as their own columns and equal Central x0.5 / x1.5 (DESNZ +-50% range); only the Central series is transcribed, selected via the Scenario/Active columns. | https://www.gov.uk/government/publications/valuation-of-energy-use-and-greenhouse-gas-emissions-for-appraisal | 2022
Carbon Value | Central | 2034 | yes | carbon_value | Appraisal carbon value 2034 [GBP(2022)/tCO2e, Central] | 312.85 | Verified assumption | DESNZ supplementary guidance: data tables data-tables-1-19.xlsx (updated 17 Apr 2023), Table 3 (Carbon values and sensitivities 2010-2100 for appraisal, 2022 GBP/tCO2e) — Central column. Low/High sensitivities are published as their own columns and equal Central x0.5 / x1.5 (DESNZ +-50% range); only the Central series is transcribed, selected via the Scenario/Active columns. | https://www.gov.uk/government/publications/valuation-of-energy-use-and-greenhouse-gas-emissions-for-appraisal | 2022
Carbon Value | Central | 2035 | yes | carbon_value | Appraisal carbon value 2035 [GBP(2022)/tCO2e, Central] | 317.62 | Verified assumption | DESNZ supplementary guidance: data tables data-tables-1-19.xlsx (updated 17 Apr 2023), Table 3 (Carbon values and sensitivities 2010-2100 for appraisal, 2022 GBP/tCO2e) — Central column. Low/High sensitivities are published as their own columns and equal Central x0.5 / x1.5 (DESNZ +-50% range); only the Central series is transcribed, selected via the Scenario/Active columns. | https://www.gov.uk/government/publications/valuation-of-energy-use-and-greenhouse-gas-emissions-for-appraisal | 2022
Carbon Value | Central | 2036 | yes | carbon_value | Appraisal carbon value 2036 [GBP(2022)/tCO2e, Central] | 322.45 | Verified assumption | DESNZ supplementary guidance: data tables data-tables-1-19.xlsx (updated 17 Apr 2023), Table 3 (Carbon values and sensitivities 2010-2100 for appraisal, 2022 GBP/tCO2e) — Central column. Low/High sensitivities are published as their own columns and equal Central x0.5 / x1.5 (DESNZ +-50% range); only the Central series is transcribed, selected via the Scenario/Active columns. | https://www.gov.uk/government/publications/valuation-of-energy-use-and-greenhouse-gas-emissions-for-appraisal | 2022
Carbon Value | Central | 2037 | yes | carbon_value | Appraisal carbon value 2037 [GBP(2022)/tCO2e, Central] | 327.36 | Verified assumption | DESNZ supplementary guidance: data tables data-tables-1-19.xlsx (updated 17 Apr 2023), Table 3 (Carbon values and sensitivities 2010-2100 for appraisal, 2022 GBP/tCO2e) — Central column. Low/High sensitivities are published as their own columns and equal Central x0.5 / x1.5 (DESNZ +-50% range); only the Central series is transcribed, selected via the Scenario/Active columns. | https://www.gov.uk/government/publications/valuation-of-energy-use-and-greenhouse-gas-emissions-for-appraisal | 2022
Carbon Value | Central | 2038 | yes | carbon_value | Appraisal carbon value 2038 [GBP(2022)/tCO2e, Central] | 332.35 | Verified assumption | DESNZ supplementary guidance: data tables data-tables-1-19.xlsx (updated 17 Apr 2023), Table 3 (Carbon values and sensitivities 2010-2100 for appraisal, 2022 GBP/tCO2e) — Central column. Low/High sensitivities are published as their own columns and equal Central x0.5 / x1.5 (DESNZ +-50% range); only the Central series is transcribed, selected via the Scenario/Active columns. | https://www.gov.uk/government/publications/valuation-of-energy-use-and-greenhouse-gas-emissions-for-appraisal | 2022
Carbon Value | Central | 2039 | yes | carbon_value | Appraisal carbon value 2039 [GBP(2022)/tCO2e, Central] | 337.41 | Verified assumption | DESNZ supplementary guidance: data tables data-tables-1-19.xlsx (updated 17 Apr 2023), Table 3 (Carbon values and sensitivities 2010-2100 for appraisal, 2022 GBP/tCO2e) — Central column. Low/High sensitivities are published as their own columns and equal Central x0.5 / x1.5 (DESNZ +-50% range); only the Central series is transcribed, selected via the Scenario/Active columns. | https://www.gov.uk/government/publications/valuation-of-energy-use-and-greenhouse-gas-emissions-for-appraisal | 2022
Note on E18: Tanya Tan: Greenhouse gas emissions values (“carbon values”) are used across government for valuing impacts on GHG emissions resulting from policy interventions. They represent a monetary value that society places on one tonne of carbon dioxide equivalent (£/tCO2e). The government uses these values to estimate a monetary value of the greenhouse gas impact of policy proposals during policy design, and also after delivery.

## PV
Key | Active | Parameter | Description (units) | Value | Type | Source | Source URL | Price Base Year
|  | module_area_m2 | Module area [m2] | 1.75 | Verified assumption | CEP Technology Library v1.02, PV (monocrystalline silicon), Panels 16-18 | https://zenodo.org/records/5758943
|  | module_kwp | Module rated power [kWp] | 0.365 | Verified assumption | CEP Technology Library v1.02, PV (monocrystalline silicon), Panels 16-18 | https://zenodo.org/records/5758943
|  | module_weight_kg | Framed module weight [kg] | 19.5 | Verified assumption | Manufacturer datasheet of Panels 16-18 from CEP Technology Library v1.02 | https://www.solarelectricsupply.com/media/custom/upload/REC-Alpha-Series-360-380W-solar-panel-datasheet.pdf
|  | efficiency | Module STC efficiency [-] | 0.209 | Verified assumption | CEP Technology Library v1.02, PV (monocrystalline silicon), Panels 16-18 | https://zenodo.org/records/5758943
|  | temp_coeff_per_C | Power temperature coefficient [/degC] | -0.0026 | Verified assumption | CEP Technology Library v1.02, PV (monocrystalline silicon), Panels 16-18 | https://zenodo.org/records/5758943
|  | ref_temp_C | STC reference temperature [degC] | 25 | Standing assumption | IEC 61215 / IEC 61853 Standard Test Conditions
|  | cell_temp_coeff | Ross coefficient, T_cell = T_amb + k*I [degC*m2/W] | 0.0256 | Verified assumption | Laksahapsoro et al. (pp 5) | https://www.sciencedirect.com/science/article/pii/S0306261925006373
|  | inverter_eff | Inverter conversion efficiency [-] | 0.97 | Verified assumption | Mondol a, Yohanis & Norton (pp 1521) | https://www.sciencedirect.com/science/article/pii/S0038092X06000600
Low |  | const_per_kwp | PV construction cost [GBP/kWp] - supply and installation of solar PV modules, supporting structures, cabling, inverters and electrical equipment | 423 | Verified assumption | DESNZ (2024) - Renewable Energy Generation Cost and Technical Assumptions – Onshore Wind and Solar PV, Section 6.3.3 - 2023 real prices | https://www.gov.uk/government/publications/onshore-wind-and-solar-cost-and-technical-assumptions | 2023
Central | yes | const_per_kwp | PV construction cost [GBP/kWp] - supply and installation of solar PV modules, supporting structures, cabling, inverters and electrical equipment | 522 | Verified assumption | DESNZ (2024) - Renewable Energy Generation Cost and Technical Assumptions – Onshore Wind and Solar PV, Section 6.3.3 - 2023 real prices | https://www.gov.uk/government/publications/onshore-wind-and-solar-cost-and-technical-assumptions | 2023
High |  | const_per_kwp | PV construction cost [GBP/kWp] - supply and installation of solar PV modules, supporting structures, cabling, inverters and electrical equipment | 601 | Verified assumption | DESNZ (2024) - Renewable Energy Generation Cost and Technical Assumptions – Onshore Wind and Solar PV, Section 6.3.3 - 2023 real prices | https://www.gov.uk/government/publications/onshore-wind-and-solar-cost-and-technical-assumptions | 2023
Low |  | infra_per_kwp | PV infrastructure cost [GBP/kWp] - grid connection, substations, and other associated infrastructure elements | 91 | Verified assumption | DESNZ (2024) - Renewable Energy Generation Cost and Technical Assumptions – Onshore Wind and Solar PV, Section 6.3.3 - 2023 real prices | https://www.gov.uk/government/publications/onshore-wind-and-solar-cost-and-technical-assumptions | 2023
Central | yes | infra_per_kwp | PV infrastructure cost [GBP/kWp] - grid connection, substations, and other associated infrastructure elements | 112 | Verified assumption | DESNZ (2024) - Renewable Energy Generation Cost and Technical Assumptions – Onshore Wind and Solar PV, Section 6.3.3 - 2023 real prices | https://www.gov.uk/government/publications/onshore-wind-and-solar-cost-and-technical-assumptions | 2023
High |  | infra_per_kwp | PV infrastructure cost [GBP/kWp] - grid connection, substations, and other associated infrastructure elements | 129 | Verified assumption | DESNZ (2024) - Renewable Energy Generation Cost and Technical Assumptions – Onshore Wind and Solar PV, Section 6.3.3 - 2023 real prices | https://www.gov.uk/government/publications/onshore-wind-and-solar-cost-and-technical-assumptions | 2023
Low |  | maint_per_mw_per_yr | PV O&M cost [GBP/MW/yr] - maintenance, logistics, monitoring expenses, e.g., module cleaning, labour, remote monitoring, spare parts, on-site inspections | 4500 | Verified assumption | DESNZ (2024) - Renewable Energy Generation Cost and Technical Assumptions – Onshore Wind and Solar PV, Section 6.3.4 - 2023 real prices | https://www.gov.uk/government/publications/onshore-wind-and-solar-cost-and-technical-assumptions | 2023
Central | yes | maint_per_mw_per_yr | PV O&M cost [GBP/MW/yr] - maintenance, logistics, monitoring expenses, e.g., module cleaning, labour, remote monitoring, spare parts, on-site inspections | 6100 | Verified assumption | DESNZ (2024) - Renewable Energy Generation Cost and Technical Assumptions – Onshore Wind and Solar PV, Section 6.3.4 - 2023 real prices | https://www.gov.uk/government/publications/onshore-wind-and-solar-cost-and-technical-assumptions | 2023
High |  | maint_per_mw_per_yr | PV O&M cost [GBP/MW/yr] - maintenance, logistics, monitoring expenses, e.g., module cleaning, labour, remote monitoring, spare parts, on-site inspections | 7600 | Verified assumption | DESNZ (2024) - Renewable Energy Generation Cost and Technical Assumptions – Onshore Wind and Solar PV, Section 6.3.4 - 2023 real prices | https://www.gov.uk/government/publications/onshore-wind-and-solar-cost-and-technical-assumptions | 2023
Low |  | insurance_per_mw_per_yr | PV insurance cost [GBP/MW/yr] | 800 | Verified assumption | DESNZ (2024) - Renewable Energy Generation Cost and Technical Assumptions – Onshore Wind and Solar PV, Section 6.3.4 - 2023 real prices | https://www.gov.uk/government/publications/onshore-wind-and-solar-cost-and-technical-assumptions | 2023
Central | yes | insurance_per_mw_per_yr | PV insurance cost [GBP/MW/yr] | 1600 | Verified assumption | DESNZ (2024) - Renewable Energy Generation Cost and Technical Assumptions – Onshore Wind and Solar PV, Section 6.3.4 - 2023 real prices | https://www.gov.uk/government/publications/onshore-wind-and-solar-cost-and-technical-assumptions | 2023
High |  | insurance_per_mw_per_yr | PV insurance cost [GBP/MW/yr] | 2700 | Verified assumption | DESNZ (2024) - Renewable Energy Generation Cost and Technical Assumptions – Onshore Wind and Solar PV, Section 6.3.4 - 2023 real prices | https://www.gov.uk/government/publications/onshore-wind-and-solar-cost-and-technical-assumptions | 2023
|  | soh_decay_per_yr | PV linear degradation [/yr] | 0.0055 | Verified assumption | Laksahapsoro et al. (pp 9) | https://www.sciencedirect.com/science/article/pii/S0306261925006373
|  | soh_inv_decay_per_yr | Inverter degradation [/yr] | 0.005 | Verified assumption | Laksahapsoro et al. (pp 9) | https://www.sciencedirect.com/science/article/pii/S0306261925006373
|  | inv_replace_year | Inverter replacement year [yr] | 10 | Verified assumption | Cayuela, et al. (pp 4) | https://www.sciencedirect.com/science/article/pii/S0048969724069705#bb0050
|  | inv_cost_share | Inverter as fraction of PV capex [-] [derivation: 230/(549+168+451+214+213+697+230+456); Q1-2025 Solar PV Cost Benchmark, Fig 2] | 0.077233 | Verified assumption | Q1-2025 Solar Photovoltaic System Cost Benchmarks (pp 4, Figure 2) | https://data.nlr.gov/submissions/304

## Battery
Parameter | Description (units) | Value | Type | Source | Source URL | Price Base Year
energy_capex_per_kwh | Li-ion energy capex [GBP/kWh] [derivation: USD 241/kWh x 0.75 USD-GBP] | 180.75 | Verified assumption | NREL (2025) - Cost Projections for Utility-Scale Battery Storage: 2025 Update | https://www.osti.gov/biblio/2583471 | 2024
power_capex_per_kw | Power capex [GBP/kW] [derivation: USD 379.16/kW x 0.75 USD-GBP] | 284.37 | Verified assumption | NREL (2025) - Cost Projections for Utility-Scale Battery Storage: 2025 Update | https://www.osti.gov/biblio/2583471 | 2024
round_trip_eff | Round-trip efficiency [-] | 0.85 | Verified assumption | NREL (2025) - Cost Projections for Utility-Scale Battery Storage: 2025 Update | https://www.osti.gov/biblio/2583471
maint_pct_capex | Battery O&M [fraction of capex /yr] | 0.04 | Verified assumption | NREL (2025) - Cost Projections for Utility-Scale Battery Storage: 2025 Update | https://www.osti.gov/biblio/2583471
replace_year | Battery replacement year [yr] | 15 | Verified assumption | NREL (2025) - Cost Projections for Utility-Scale Battery Storage: 2025 Update | https://www.osti.gov/biblio/2583471
soh_decay_per_yr | Battery (LFP) degradation, geometric SOH (1-delta)^y [/yr] | 0.0267 | Verified assumption | Laksahapsoro et al. (2025) - LFP battery degradation rate (Table 4, delta_b^batt) | https://www.sciencedirect.com/science/article/pii/S0306261925006373
soc_min | Minimum usable SOC [-] | 0.1 | Standing assumption | - (operational DoD choice; within manufacturer usable-DoD range)
soc_max | Maximum usable SOC [-] | 0.9 | Standing assumption | - (operational DoD choice)
c_rate_chg | Charge C-rate [1/h] | 0.5 | Standing assumption | - (system design choice; cf. 1-4h system datasheets)
c_rate_disc | Discharge C-rate [1/h] | 0.5 | Standing assumption | - (system design choice)

## Heating
Scope | Parameter | Description (units) | Value | Type | Source | Source URL | Price Base Year
Gas Boiler | capex_per_kwth | Boiler capex, including preparatory works, installation, completion, and sundries [GBP/kW_th] | 260 | Verified assumption | Evidence update of low carbon heating and cooling in non-domestic buildings | https://www.gov.uk/government/publications/evidence-update-of-low-carbon-heating-and-cooling-in-non-domestic-buildings | 2019
Gas Boiler | maint_per_kwth_per_yr | O&M [GBP/kW_th/yr] | 6 | Verified assumption | Evidence update of low carbon heating and cooling in non-domestic buildings | https://www.gov.uk/government/publications/evidence-update-of-low-carbon-heating-and-cooling-in-non-domestic-buildings | 2019
Gas Boiler | replace_year | Plant lifetime [yr] | 15 | Verified assumption | Evidence update of low carbon heating and cooling in non-domestic buildings | https://www.gov.uk/government/publications/evidence-update-of-low-carbon-heating-and-cooling-in-non-domestic-buildings
Gas Boiler | replace_cost_share | Fraction of equipment replaced [-] | 1 | Verified assumption | - (whole unit replaced)
ASHP | capex_per_kwth | ASHP (air-to-water) capex [GBP/kW_th] | 1530 | Verified assumption | Evidence update of low carbon heating and cooling in non-domestic buildings | https://www.gov.uk/government/publications/evidence-update-of-low-carbon-heating-and-cooling-in-non-domestic-buildings | 2019
ASHP | maint_per_kwth_per_yr | O&M [GBP/kW_th/yr] | 6 | Verified assumption | Evidence update of low carbon heating and cooling in non-domestic buildings | https://www.gov.uk/government/publications/evidence-update-of-low-carbon-heating-and-cooling-in-non-domestic-buildings | 2019
ASHP | replace_year | Plant lifetime [yr] | 20 | Verified assumption | Evidence update of low carbon heating and cooling in non-domestic buildings | https://www.gov.uk/government/publications/evidence-update-of-low-carbon-heating-and-cooling-in-non-domestic-buildings
ASHP | replace_cost_share | Fraction of equipment replaced [-] | 1 | Verified assumption | - (whole unit replaced)
GSHP (vertical) | capex_per_kwth | GSHP-V capex [GBP/kW_th] | 2690 | Verified assumption | Evidence update of low carbon heating and cooling in non-domestic buildings | https://www.gov.uk/government/publications/evidence-update-of-low-carbon-heating-and-cooling-in-non-domestic-buildings | 2019
GSHP (vertical) | maint_per_kwth_per_yr | O&M [GBP/kW_th/yr] | 6 | Verified assumption | Evidence update of low carbon heating and cooling in non-domestic buildings | https://www.gov.uk/government/publications/evidence-update-of-low-carbon-heating-and-cooling-in-non-domestic-buildings | 2019
GSHP (vertical) | replace_year | HP unit lifetime [yr] | 20 | Verified assumption | Evidence update of low carbon heating and cooling in non-domestic buildings | https://www.gov.uk/government/publications/evidence-update-of-low-carbon-heating-and-cooling-in-non-domestic-buildings
GSHP (vertical) | replace_cost_share | HP-unit share of capex (loop outlasts) [-] | 0.569 | Standing assumption | DERIVED. Heat-pump-unit share of capex re-incurred at replacement, since ground loop outlasts the unit. Derived by treating the air-water HP total (1,530/kW_th) as the non-loop cost: 1,530/2,690 = 0.569. | https://www.gov.uk/government/publications/evidence-update-of-low-carbon-heating-and-cooling-in-non-domestic-buildings
GSHP (horizontal) | capex_per_kwth | GSHP-H capex [GBP/kW_th] | 1699 | Standing assumption | DERIVED. Ratio from GSHP Association installed-cost ranges: horizontal GBP 1,250-1,750/kW vs vertical GBP 1,750-3,000/kW; midpoint ratio 1,500/2,375 = 0.6316. GSHP capex GBP 2,690/kW_th (2019, excl VAT) x 0.6316 horizontal/vertical cost ratio = GBP 1,699/kW_th. | https://www.gov.uk/government/publications/evidence-update-of-low-carbon-heating-and-cooling-in-non-domestic-buildings | 2019
GSHP (horizontal) | maint_per_kwth_per_yr | O&M [GBP/kW_th/yr] | 6 | Verified assumption | Evidence update of low carbon heating and cooling in non-domestic buildings | https://www.gov.uk/government/publications/evidence-update-of-low-carbon-heating-and-cooling-in-non-domestic-buildings | 2019
GSHP (horizontal) | replace_year | HP unit lifetime [yr] | 20 | Verified assumption | Evidence update of low carbon heating and cooling in non-domestic buildings | https://www.gov.uk/government/publications/evidence-update-of-low-carbon-heating-and-cooling-in-non-domestic-buildings
GSHP (horizontal) | replace_cost_share | HP-unit share of capex (loop outlasts) [-] | 0.901 | Standing assumption | DERIVED. As GSHP (vertical), but against the discounted horizontal capex -- 1,530/1,699 = 0.901.
Gas Boiler | decommission_fixed | One-off fixed cost to disconnect the gas service in a retrofit [GBP/site, excl. VAT] (only if NEW_BUILD=False and new scenario is heat pump). CONSERVATIVE: uses the 125mm service rate, above the typical non-domestic 90mm. | 2455 | Verified assumption | Cadent Connections Charging Statement, 1 April 2024 (pp 5 Table 3 - Standard Service Disconnection Charges (excl. VAT); 125mm PE/4in, conservative value (East Midlands/North West/West Midlands networks)) | https://cadentgas.com/getmedia/d0d1ff01-6b02-41c6-a7d1-99a5f89da2a4/connections-charging-statement-01-april-2024.pdf | 2024

## Thermal Store
Parameter | Description (units) | Value | Type | Source | Source URL | Price Base Year
energy_capex_per_kwh | Buffer-tank capex [GBP/kWh_th] [derivation: EUR 10/kWh x 0.85 EUR-GBP] | 8.5 | Verified assumption | IEA Technology: Sensible Heat Water Storage (pp 4) | https://iea-es.org/wp-content/uploads/public/FactSheet_Thermal_Sensible_Water_2024-07-10.pdf | 2024
standing_loss_per_step | Standing heat loss [/half-hour] | 0.0005 | Verified assumption | IEA Technology: Sensible Heat Water Storage (pp 4) | https://iea-es.org/wp-content/uploads/public/FactSheet_Thermal_Sensible_Water_2024-07-10.pdf
maint_pct_capex | O&M [fraction of capex /yr] | 0.01 | Verified assumption | Danish Energy Agency, Datasheet for energy storage (141a TTES): Fixed O&M 10.3 EUR/MWh/yr on 3.8 EUR/kWh investment ~= 0.3%/yr; rounded up to 1% as conservative small-buffer assumption | https://ens.dk/media/6589/download
replace_year | Replacement year [yr] | 40 | Verified assumption | Danish Energy Agency, Datasheet for energy storage (141a TTES) | https://ens.dk/media/6589/download
chg_eff | Charge efficiency [-] | 0.99 | Standing assumption | - (near-unity buffer tank)
disc_eff | Discharge efficiency [-] | 0.99 | Standing assumption | - (near-unity buffer tank)
soc_min | Minimum SOC [-] | 0 | Standing assumption | - (tank fully dischargeable)
soc_max | Maximum SOC [-] | 0.95 | Standing assumption | - (usable headroom)
c_rate | Charge/discharge C-rate [1/h] | 1 | Standing assumption | - (design choice)

## Roof
Scope | Parameter | Description (units) | Value | Type | Source | Source URL
Health: Hospital | pv_usable_frac | Usable roof footprint fraction - building-clutter derate [-] Derivation: pv_usable_frac = UF_Arch/Str × UF_Services × UF_Misc × UF_Maint × UF_Shadow(South) | 0.454 | Verified assumption | Ghaleb & Asif (2022) (pp 13, Table 6, South) Field survey of 117 Saudi commercial buildings (54 malls, 43 offices, 15 hotels, 5 hospitals), audited via remote sensing + site visits. Note: hot-climate/all-flat-roof context. | https://www.sciencedirect.com/science/article/pii/S0378778821010586
Health: Hospital | pv_inter_row_frac | Flat-roof array inter-row spacing. Applies to the flat-roof portion of roof_usable_frac only; pitched-roof PV mounted flush to the existing slope. | 0.41 | Verified assumption | Ghaleb & Asif (2022) (pp 13, Table 6, South) Field survey of 117 Saudi commercial buildings (54 malls, 43 offices, 15 hotels, 5 hospitals), audited via remote sensing + site visits. Note: hot-climate/all-flat-roof context. | https://www.sciencedirect.com/science/article/pii/S0378778821010586
All | ROOF_LOAD_KG_PER_M2 | Roof imposed-load allowance available for PV [kg/m2]. UK NA category H distributed imposed load qk = 0.6 kN/m2 converted at g = 9.81 m/s2. | 61.2 | Verified assumption | EN 1991-1-1: Eurocode 1: Actions on structures (pp 29, Table 6.10) | https://www.phd.eng.br/wp-content/uploads/2015/12/en.1991.1.1.2002.pdf
All | ROOF_PITCH_DEG | Typical roof pitch [deg] | 30 | Standing assumption | OSM-derived typical
All | PITCHED_USABLE_SLOPE_FRAC | Pitched-roof orientation/margin fraction - the useful-oriented share of a dual-pitch roof. | 0.4 | Verified assumption | IEA PVPS (pp 6) usable-slope guidance | https://iea-pvps.org/wp-content/uploads/2020/01/rep7_04.pdf

## GHI
District | Month | Parameter | Description (units) | Value | Type | Source | Source URL
East Anglia | January | MONTHLY_GHI | Daily GHI, East Anglia (Norwich) [kWh/m2/day] | 0.749 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, Norwich EGSH | https://re.jrc.ec.europa.eu/pvg_tools/en/
East Anglia | February | MONTHLY_GHI | Daily GHI, East Anglia (Norwich) [kWh/m2/day] | 1.388 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, Norwich EGSH | https://re.jrc.ec.europa.eu/pvg_tools/en/
East Anglia | March | MONTHLY_GHI | Daily GHI, East Anglia (Norwich) [kWh/m2/day] | 2.575 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, Norwich EGSH | https://re.jrc.ec.europa.eu/pvg_tools/en/
East Anglia | April | MONTHLY_GHI | Daily GHI, East Anglia (Norwich) [kWh/m2/day] | 4.211 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, Norwich EGSH | https://re.jrc.ec.europa.eu/pvg_tools/en/
East Anglia | May | MONTHLY_GHI | Daily GHI, East Anglia (Norwich) [kWh/m2/day] | 4.892 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, Norwich EGSH | https://re.jrc.ec.europa.eu/pvg_tools/en/
East Anglia | June | MONTHLY_GHI | Daily GHI, East Anglia (Norwich) [kWh/m2/day] | 5.261 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, Norwich EGSH | https://re.jrc.ec.europa.eu/pvg_tools/en/
East Anglia | July | MONTHLY_GHI | Daily GHI, East Anglia (Norwich) [kWh/m2/day] | 5.132 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, Norwich EGSH | https://re.jrc.ec.europa.eu/pvg_tools/en/
East Anglia | August | MONTHLY_GHI | Daily GHI, East Anglia (Norwich) [kWh/m2/day] | 4.334 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, Norwich EGSH | https://re.jrc.ec.europa.eu/pvg_tools/en/
East Anglia | September | MONTHLY_GHI | Daily GHI, East Anglia (Norwich) [kWh/m2/day] | 3.226 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, Norwich EGSH | https://re.jrc.ec.europa.eu/pvg_tools/en/
East Anglia | October | MONTHLY_GHI | Daily GHI, East Anglia (Norwich) [kWh/m2/day] | 1.809 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, Norwich EGSH | https://re.jrc.ec.europa.eu/pvg_tools/en/
East Anglia | November | MONTHLY_GHI | Daily GHI, East Anglia (Norwich) [kWh/m2/day] | 0.963 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, Norwich EGSH | https://re.jrc.ec.europa.eu/pvg_tools/en/
East Anglia | December | MONTHLY_GHI | Daily GHI, East Anglia (Norwich) [kWh/m2/day] | 0.609 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, Norwich EGSH | https://re.jrc.ec.europa.eu/pvg_tools/en/
England E and NE | January | MONTHLY_GHI | Daily GHI, England E and NE (Newcastle) [kWh/m2/day] | 0.608 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, Newcastle EGNT | https://re.jrc.ec.europa.eu/pvg_tools/en/
England E and NE | February | MONTHLY_GHI | Daily GHI, England E and NE (Newcastle) [kWh/m2/day] | 1.256 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, Newcastle EGNT | https://re.jrc.ec.europa.eu/pvg_tools/en/
England E and NE | March | MONTHLY_GHI | Daily GHI, England E and NE (Newcastle) [kWh/m2/day] | 2.365 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, Newcastle EGNT | https://re.jrc.ec.europa.eu/pvg_tools/en/
England E and NE | April | MONTHLY_GHI | Daily GHI, England E and NE (Newcastle) [kWh/m2/day] | 3.807 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, Newcastle EGNT | https://re.jrc.ec.europa.eu/pvg_tools/en/
England E and NE | May | MONTHLY_GHI | Daily GHI, England E and NE (Newcastle) [kWh/m2/day] | 4.66 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, Newcastle EGNT | https://re.jrc.ec.europa.eu/pvg_tools/en/
England E and NE | June | MONTHLY_GHI | Daily GHI, England E and NE (Newcastle) [kWh/m2/day] | 4.847 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, Newcastle EGNT | https://re.jrc.ec.europa.eu/pvg_tools/en/
England E and NE | July | MONTHLY_GHI | Daily GHI, England E and NE (Newcastle) [kWh/m2/day] | 4.723 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, Newcastle EGNT | https://re.jrc.ec.europa.eu/pvg_tools/en/
England E and NE | August | MONTHLY_GHI | Daily GHI, England E and NE (Newcastle) [kWh/m2/day] | 3.92 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, Newcastle EGNT | https://re.jrc.ec.europa.eu/pvg_tools/en/
England E and NE | September | MONTHLY_GHI | Daily GHI, England E and NE (Newcastle) [kWh/m2/day] | 2.833 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, Newcastle EGNT | https://re.jrc.ec.europa.eu/pvg_tools/en/
England E and NE | October | MONTHLY_GHI | Daily GHI, England E and NE (Newcastle) [kWh/m2/day] | 1.532 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, Newcastle EGNT | https://re.jrc.ec.europa.eu/pvg_tools/en/
England E and NE | November | MONTHLY_GHI | Daily GHI, England E and NE (Newcastle) [kWh/m2/day] | 0.802 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, Newcastle EGNT | https://re.jrc.ec.europa.eu/pvg_tools/en/
England E and NE | December | MONTHLY_GHI | Daily GHI, England E and NE (Newcastle) [kWh/m2/day] | 0.462 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, Newcastle EGNT | https://re.jrc.ec.europa.eu/pvg_tools/en/
England NW and N Wales | January | MONTHLY_GHI | Daily GHI, England NW and N Wales (Manchester) [kWh/m2/day] | 0.6 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, Manchester EGCC | https://re.jrc.ec.europa.eu/pvg_tools/en/
England NW and N Wales | February | MONTHLY_GHI | Daily GHI, England NW and N Wales (Manchester) [kWh/m2/day] | 1.25 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, Manchester EGCC | https://re.jrc.ec.europa.eu/pvg_tools/en/
England NW and N Wales | March | MONTHLY_GHI | Daily GHI, England NW and N Wales (Manchester) [kWh/m2/day] | 2.367 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, Manchester EGCC | https://re.jrc.ec.europa.eu/pvg_tools/en/
England NW and N Wales | April | MONTHLY_GHI | Daily GHI, England NW and N Wales (Manchester) [kWh/m2/day] | 3.787 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, Manchester EGCC | https://re.jrc.ec.europa.eu/pvg_tools/en/
England NW and N Wales | May | MONTHLY_GHI | Daily GHI, England NW and N Wales (Manchester) [kWh/m2/day] | 4.512 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, Manchester EGCC | https://re.jrc.ec.europa.eu/pvg_tools/en/
England NW and N Wales | June | MONTHLY_GHI | Daily GHI, England NW and N Wales (Manchester) [kWh/m2/day] | 4.868 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, Manchester EGCC | https://re.jrc.ec.europa.eu/pvg_tools/en/
England NW and N Wales | July | MONTHLY_GHI | Daily GHI, England NW and N Wales (Manchester) [kWh/m2/day] | 4.594 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, Manchester EGCC | https://re.jrc.ec.europa.eu/pvg_tools/en/
England NW and N Wales | August | MONTHLY_GHI | Daily GHI, England NW and N Wales (Manchester) [kWh/m2/day] | 3.838 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, Manchester EGCC | https://re.jrc.ec.europa.eu/pvg_tools/en/
England NW and N Wales | September | MONTHLY_GHI | Daily GHI, England NW and N Wales (Manchester) [kWh/m2/day] | 2.813 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, Manchester EGCC | https://re.jrc.ec.europa.eu/pvg_tools/en/
England NW and N Wales | October | MONTHLY_GHI | Daily GHI, England NW and N Wales (Manchester) [kWh/m2/day] | 1.582 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, Manchester EGCC | https://re.jrc.ec.europa.eu/pvg_tools/en/
England NW and N Wales | November | MONTHLY_GHI | Daily GHI, England NW and N Wales (Manchester) [kWh/m2/day] | 0.826 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, Manchester EGCC | https://re.jrc.ec.europa.eu/pvg_tools/en/
England NW and N Wales | December | MONTHLY_GHI | Daily GHI, England NW and N Wales (Manchester) [kWh/m2/day] | 0.51 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, Manchester EGCC | https://re.jrc.ec.europa.eu/pvg_tools/en/
England SE and Central S | January | MONTHLY_GHI | Daily GHI, England SE and Central S (London Heathrow) [kWh/m2/day] | 0.822 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, London Heathrow EGLL | https://re.jrc.ec.europa.eu/pvg_tools/en/
England SE and Central S | February | MONTHLY_GHI | Daily GHI, England SE and Central S (London Heathrow) [kWh/m2/day] | 1.46 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, London Heathrow EGLL | https://re.jrc.ec.europa.eu/pvg_tools/en/
England SE and Central S | March | MONTHLY_GHI | Daily GHI, England SE and Central S (London Heathrow) [kWh/m2/day] | 2.6 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, London Heathrow EGLL | https://re.jrc.ec.europa.eu/pvg_tools/en/
England SE and Central S | April | MONTHLY_GHI | Daily GHI, England SE and Central S (London Heathrow) [kWh/m2/day] | 4.174 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, London Heathrow EGLL | https://re.jrc.ec.europa.eu/pvg_tools/en/
England SE and Central S | May | MONTHLY_GHI | Daily GHI, England SE and Central S (London Heathrow) [kWh/m2/day] | 4.861 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, London Heathrow EGLL | https://re.jrc.ec.europa.eu/pvg_tools/en/
England SE and Central S | June | MONTHLY_GHI | Daily GHI, England SE and Central S (London Heathrow) [kWh/m2/day] | 5.391 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, London Heathrow EGLL | https://re.jrc.ec.europa.eu/pvg_tools/en/
England SE and Central S | July | MONTHLY_GHI | Daily GHI, England SE and Central S (London Heathrow) [kWh/m2/day] | 5.252 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, London Heathrow EGLL | https://re.jrc.ec.europa.eu/pvg_tools/en/
England SE and Central S | August | MONTHLY_GHI | Daily GHI, England SE and Central S (London Heathrow) [kWh/m2/day] | 4.333 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, London Heathrow EGLL | https://re.jrc.ec.europa.eu/pvg_tools/en/
England SE and Central S | September | MONTHLY_GHI | Daily GHI, England SE and Central S (London Heathrow) [kWh/m2/day] | 3.26 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, London Heathrow EGLL | https://re.jrc.ec.europa.eu/pvg_tools/en/
England SE and Central S | October | MONTHLY_GHI | Daily GHI, England SE and Central S (London Heathrow) [kWh/m2/day] | 1.885 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, London Heathrow EGLL | https://re.jrc.ec.europa.eu/pvg_tools/en/
England SE and Central S | November | MONTHLY_GHI | Daily GHI, England SE and Central S (London Heathrow) [kWh/m2/day] | 1.044 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, London Heathrow EGLL | https://re.jrc.ec.europa.eu/pvg_tools/en/
England SE and Central S | December | MONTHLY_GHI | Daily GHI, England SE and Central S (London Heathrow) [kWh/m2/day] | 0.664 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, London Heathrow EGLL | https://re.jrc.ec.europa.eu/pvg_tools/en/
England SW and S Wales | January | MONTHLY_GHI | Daily GHI, England SW and S Wales (Exeter) [kWh/m2/day] | 0.855 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, Exeter EGTE | https://re.jrc.ec.europa.eu/pvg_tools/en/
England SW and S Wales | February | MONTHLY_GHI | Daily GHI, England SW and S Wales (Exeter) [kWh/m2/day] | 1.571 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, Exeter EGTE | https://re.jrc.ec.europa.eu/pvg_tools/en/
England SW and S Wales | March | MONTHLY_GHI | Daily GHI, England SW and S Wales (Exeter) [kWh/m2/day] | 2.728 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, Exeter EGTE | https://re.jrc.ec.europa.eu/pvg_tools/en/
England SW and S Wales | April | MONTHLY_GHI | Daily GHI, England SW and S Wales (Exeter) [kWh/m2/day] | 4.353 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, Exeter EGTE | https://re.jrc.ec.europa.eu/pvg_tools/en/
England SW and S Wales | May | MONTHLY_GHI | Daily GHI, England SW and S Wales (Exeter) [kWh/m2/day] | 5.083 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, Exeter EGTE | https://re.jrc.ec.europa.eu/pvg_tools/en/
England SW and S Wales | June | MONTHLY_GHI | Daily GHI, England SW and S Wales (Exeter) [kWh/m2/day] | 5.49 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, Exeter EGTE | https://re.jrc.ec.europa.eu/pvg_tools/en/
England SW and S Wales | July | MONTHLY_GHI | Daily GHI, England SW and S Wales (Exeter) [kWh/m2/day] | 5.26 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, Exeter EGTE | https://re.jrc.ec.europa.eu/pvg_tools/en/
England SW and S Wales | August | MONTHLY_GHI | Daily GHI, England SW and S Wales (Exeter) [kWh/m2/day] | 4.377 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, Exeter EGTE | https://re.jrc.ec.europa.eu/pvg_tools/en/
England SW and S Wales | September | MONTHLY_GHI | Daily GHI, England SW and S Wales (Exeter) [kWh/m2/day] | 3.295 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, Exeter EGTE | https://re.jrc.ec.europa.eu/pvg_tools/en/
England SW and S Wales | October | MONTHLY_GHI | Daily GHI, England SW and S Wales (Exeter) [kWh/m2/day] | 1.89 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, Exeter EGTE | https://re.jrc.ec.europa.eu/pvg_tools/en/
England SW and S Wales | November | MONTHLY_GHI | Daily GHI, England SW and S Wales (Exeter) [kWh/m2/day] | 1.097 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, Exeter EGTE | https://re.jrc.ec.europa.eu/pvg_tools/en/
England SW and S Wales | December | MONTHLY_GHI | Daily GHI, England SW and S Wales (Exeter) [kWh/m2/day] | 0.692 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, Exeter EGTE | https://re.jrc.ec.europa.eu/pvg_tools/en/
Midlands | January | MONTHLY_GHI | Daily GHI, Midlands (Birmingham) [kWh/m2/day] | 0.731 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, Birmingham EGBB | https://re.jrc.ec.europa.eu/pvg_tools/en/
Midlands | February | MONTHLY_GHI | Daily GHI, Midlands (Birmingham) [kWh/m2/day] | 1.385 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, Birmingham EGBB | https://re.jrc.ec.europa.eu/pvg_tools/en/
Midlands | March | MONTHLY_GHI | Daily GHI, Midlands (Birmingham) [kWh/m2/day] | 2.494 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, Birmingham EGBB | https://re.jrc.ec.europa.eu/pvg_tools/en/
Midlands | April | MONTHLY_GHI | Daily GHI, Midlands (Birmingham) [kWh/m2/day] | 3.936 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, Birmingham EGBB | https://re.jrc.ec.europa.eu/pvg_tools/en/
Midlands | May | MONTHLY_GHI | Daily GHI, Midlands (Birmingham) [kWh/m2/day] | 4.691 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, Birmingham EGBB | https://re.jrc.ec.europa.eu/pvg_tools/en/
Midlands | June | MONTHLY_GHI | Daily GHI, Midlands (Birmingham) [kWh/m2/day] | 5.113 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, Birmingham EGBB | https://re.jrc.ec.europa.eu/pvg_tools/en/
Midlands | July | MONTHLY_GHI | Daily GHI, Midlands (Birmingham) [kWh/m2/day] | 4.989 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, Birmingham EGBB | https://re.jrc.ec.europa.eu/pvg_tools/en/
Midlands | August | MONTHLY_GHI | Daily GHI, Midlands (Birmingham) [kWh/m2/day] | 4.106 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, Birmingham EGBB | https://re.jrc.ec.europa.eu/pvg_tools/en/
Midlands | September | MONTHLY_GHI | Daily GHI, Midlands (Birmingham) [kWh/m2/day] | 3.082 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, Birmingham EGBB | https://re.jrc.ec.europa.eu/pvg_tools/en/
Midlands | October | MONTHLY_GHI | Daily GHI, Midlands (Birmingham) [kWh/m2/day] | 1.721 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, Birmingham EGBB | https://re.jrc.ec.europa.eu/pvg_tools/en/
Midlands | November | MONTHLY_GHI | Daily GHI, Midlands (Birmingham) [kWh/m2/day] | 0.929 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, Birmingham EGBB | https://re.jrc.ec.europa.eu/pvg_tools/en/
Midlands | December | MONTHLY_GHI | Daily GHI, Midlands (Birmingham) [kWh/m2/day] | 0.599 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, Birmingham EGBB | https://re.jrc.ec.europa.eu/pvg_tools/en/
Scotland E | January | MONTHLY_GHI | Daily GHI, Scotland E (Edinburgh) [kWh/m2/day] | 0.503 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, Edinburgh EGPH | https://re.jrc.ec.europa.eu/pvg_tools/en/
Scotland E | February | MONTHLY_GHI | Daily GHI, Scotland E (Edinburgh) [kWh/m2/day] | 1.13 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, Edinburgh EGPH | https://re.jrc.ec.europa.eu/pvg_tools/en/
Scotland E | March | MONTHLY_GHI | Daily GHI, Scotland E (Edinburgh) [kWh/m2/day] | 2.196 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, Edinburgh EGPH | https://re.jrc.ec.europa.eu/pvg_tools/en/
Scotland E | April | MONTHLY_GHI | Daily GHI, Scotland E (Edinburgh) [kWh/m2/day] | 3.714 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, Edinburgh EGPH | https://re.jrc.ec.europa.eu/pvg_tools/en/
Scotland E | May | MONTHLY_GHI | Daily GHI, Scotland E (Edinburgh) [kWh/m2/day] | 4.585 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, Edinburgh EGPH | https://re.jrc.ec.europa.eu/pvg_tools/en/
Scotland E | June | MONTHLY_GHI | Daily GHI, Scotland E (Edinburgh) [kWh/m2/day] | 4.758 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, Edinburgh EGPH | https://re.jrc.ec.europa.eu/pvg_tools/en/
Scotland E | July | MONTHLY_GHI | Daily GHI, Scotland E (Edinburgh) [kWh/m2/day] | 4.645 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, Edinburgh EGPH | https://re.jrc.ec.europa.eu/pvg_tools/en/
Scotland E | August | MONTHLY_GHI | Daily GHI, Scotland E (Edinburgh) [kWh/m2/day] | 3.802 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, Edinburgh EGPH | https://re.jrc.ec.europa.eu/pvg_tools/en/
Scotland E | September | MONTHLY_GHI | Daily GHI, Scotland E (Edinburgh) [kWh/m2/day] | 2.698 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, Edinburgh EGPH | https://re.jrc.ec.europa.eu/pvg_tools/en/
Scotland E | October | MONTHLY_GHI | Daily GHI, Scotland E (Edinburgh) [kWh/m2/day] | 1.446 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, Edinburgh EGPH | https://re.jrc.ec.europa.eu/pvg_tools/en/
Scotland E | November | MONTHLY_GHI | Daily GHI, Scotland E (Edinburgh) [kWh/m2/day] | 0.73 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, Edinburgh EGPH | https://re.jrc.ec.europa.eu/pvg_tools/en/
Scotland E | December | MONTHLY_GHI | Daily GHI, Scotland E (Edinburgh) [kWh/m2/day] | 0.369 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, Edinburgh EGPH | https://re.jrc.ec.europa.eu/pvg_tools/en/
Scotland N | January | MONTHLY_GHI | Daily GHI, Scotland N (Inverness) [kWh/m2/day] | 0.377 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, Inverness EGPE | https://re.jrc.ec.europa.eu/pvg_tools/en/
Scotland N | February | MONTHLY_GHI | Daily GHI, Scotland N (Inverness) [kWh/m2/day] | 1.018 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, Inverness EGPE | https://re.jrc.ec.europa.eu/pvg_tools/en/
Scotland N | March | MONTHLY_GHI | Daily GHI, Scotland N (Inverness) [kWh/m2/day] | 2.083 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, Inverness EGPE | https://re.jrc.ec.europa.eu/pvg_tools/en/
Scotland N | April | MONTHLY_GHI | Daily GHI, Scotland N (Inverness) [kWh/m2/day] | 3.534 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, Inverness EGPE | https://re.jrc.ec.europa.eu/pvg_tools/en/
Scotland N | May | MONTHLY_GHI | Daily GHI, Scotland N (Inverness) [kWh/m2/day] | 4.387 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, Inverness EGPE | https://re.jrc.ec.europa.eu/pvg_tools/en/
Scotland N | June | MONTHLY_GHI | Daily GHI, Scotland N (Inverness) [kWh/m2/day] | 4.588 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, Inverness EGPE | https://re.jrc.ec.europa.eu/pvg_tools/en/
Scotland N | July | MONTHLY_GHI | Daily GHI, Scotland N (Inverness) [kWh/m2/day] | 4.399 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, Inverness EGPE | https://re.jrc.ec.europa.eu/pvg_tools/en/
Scotland N | August | MONTHLY_GHI | Daily GHI, Scotland N (Inverness) [kWh/m2/day] | 3.612 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, Inverness EGPE | https://re.jrc.ec.europa.eu/pvg_tools/en/
Scotland N | September | MONTHLY_GHI | Daily GHI, Scotland N (Inverness) [kWh/m2/day] | 2.573 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, Inverness EGPE | https://re.jrc.ec.europa.eu/pvg_tools/en/
Scotland N | October | MONTHLY_GHI | Daily GHI, Scotland N (Inverness) [kWh/m2/day] | 1.352 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, Inverness EGPE | https://re.jrc.ec.europa.eu/pvg_tools/en/
Scotland N | November | MONTHLY_GHI | Daily GHI, Scotland N (Inverness) [kWh/m2/day] | 0.581 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, Inverness EGPE | https://re.jrc.ec.europa.eu/pvg_tools/en/
Scotland N | December | MONTHLY_GHI | Daily GHI, Scotland N (Inverness) [kWh/m2/day] | 0.266 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, Inverness EGPE | https://re.jrc.ec.europa.eu/pvg_tools/en/
Scotland W | January | MONTHLY_GHI | Daily GHI, Scotland W (Glasgow Prestwick) [kWh/m2/day] | 0.48 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, Glasgow Prestwick EGPK | https://re.jrc.ec.europa.eu/pvg_tools/en/
Scotland W | February | MONTHLY_GHI | Daily GHI, Scotland W (Glasgow Prestwick) [kWh/m2/day] | 1.103 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, Glasgow Prestwick EGPK | https://re.jrc.ec.europa.eu/pvg_tools/en/
Scotland W | March | MONTHLY_GHI | Daily GHI, Scotland W (Glasgow Prestwick) [kWh/m2/day] | 2.214 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, Glasgow Prestwick EGPK | https://re.jrc.ec.europa.eu/pvg_tools/en/
Scotland W | April | MONTHLY_GHI | Daily GHI, Scotland W (Glasgow Prestwick) [kWh/m2/day] | 3.858 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, Glasgow Prestwick EGPK | https://re.jrc.ec.europa.eu/pvg_tools/en/
Scotland W | May | MONTHLY_GHI | Daily GHI, Scotland W (Glasgow Prestwick) [kWh/m2/day] | 4.774 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, Glasgow Prestwick EGPK | https://re.jrc.ec.europa.eu/pvg_tools/en/
Scotland W | June | MONTHLY_GHI | Daily GHI, Scotland W (Glasgow Prestwick) [kWh/m2/day] | 4.918 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, Glasgow Prestwick EGPK | https://re.jrc.ec.europa.eu/pvg_tools/en/
Scotland W | July | MONTHLY_GHI | Daily GHI, Scotland W (Glasgow Prestwick) [kWh/m2/day] | 4.668 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, Glasgow Prestwick EGPK | https://re.jrc.ec.europa.eu/pvg_tools/en/
Scotland W | August | MONTHLY_GHI | Daily GHI, Scotland W (Glasgow Prestwick) [kWh/m2/day] | 3.828 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, Glasgow Prestwick EGPK | https://re.jrc.ec.europa.eu/pvg_tools/en/
Scotland W | September | MONTHLY_GHI | Daily GHI, Scotland W (Glasgow Prestwick) [kWh/m2/day] | 2.609 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, Glasgow Prestwick EGPK | https://re.jrc.ec.europa.eu/pvg_tools/en/
Scotland W | October | MONTHLY_GHI | Daily GHI, Scotland W (Glasgow Prestwick) [kWh/m2/day] | 1.404 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, Glasgow Prestwick EGPK | https://re.jrc.ec.europa.eu/pvg_tools/en/
Scotland W | November | MONTHLY_GHI | Daily GHI, Scotland W (Glasgow Prestwick) [kWh/m2/day] | 0.698 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, Glasgow Prestwick EGPK | https://re.jrc.ec.europa.eu/pvg_tools/en/
Scotland W | December | MONTHLY_GHI | Daily GHI, Scotland W (Glasgow Prestwick) [kWh/m2/day] | 0.367 | Verified assumption | PVGIS (EC JRC) SARAH3 long-term monthly average 2005-2023, Glasgow Prestwick EGPK | https://re.jrc.ec.europa.eu/pvg_tools/en/

## Heating & COP (DM)
Parameter | Description (units) | Value | Type | Source | Source URL
ETA_BOILER | Gas-boiler gross seasonal efficiency, GCV basis [-] | 0.925 | Verified assumption | Commission Regulation (EU) No 813/2013 | https://www.legislation.gov.uk/eur/2013/813/annex/II
ashp_cop_at_7C | ASHP COP at 7 degC outdoor (intercept) [-] | 2.7283 | Verified assumption | CEP Technology Library v1.02, HP air-water (Heating), Company 4 R-32 | https://zenodo.org/records/5758943
ashp_cop_slope_per_C | ASHP COP slope vs outdoor temp [/degC] | 0.071267 | Verified assumption | CEP Technology Library v1.02 (Company 4 R-32 fitted slope) | https://zenodo.org/records/5758943
gshp_cop_at_10C | GSHP COP at 10 degC brine (anchor) [-] | 3.23 | Verified assumption | CEP Technology Library v1.02, HP ground-water (Heating), Company 1 (49-75 kW) | https://zenodo.org/records/5758943
gshp_cop_slope_per_C | GSHP COP slope vs brine temp [/degC] | 0.04598 | Verified assumption | CEP Technology Library v1.02 (Company 1 fitted slope) | https://zenodo.org/records/5758943
T_ASHP_MIN | ASHP min operating outdoor temp [degC] | -20 | Verified assumption | CEP Technology Library v1.02 (Company 4 R32, WO=45 envelope) | https://zenodo.org/records/5758943
T_ASHP_MAX | ASHP max operating outdoor temp [degC] | 20 | Verified assumption | CEP Technology Library v1.02 (Company 4 R32, WO=45 envelope) | https://zenodo.org/records/5758943
T_GSHP_MIN | GSHP min brine inlet temp [degC] | -5 | Verified assumption | CEP Technology Library v1.02 (Company 1, WO=45 envelope) | https://zenodo.org/records/5758943
T_GSHP_MAX | GSHP max brine inlet temp [degC] | 20 | Verified assumption | CEP Technology Library v1.02 (Company 1, WO=45 envelope) | https://zenodo.org/records/5758943

## Ground Loop (DM)
Parameter | Description (units) | Value | Type | Source | Source URL
HORIZONTAL_LOOP_DEPTH_M | Horizontal slinky burial depth [m] | 1.5 | Verified assumption | David Banks - An Introduction to Thermogeology: Ground Source Heating and Cooling (pp 186-188, Section 8.1 Depth of burial) | https://onlinelibrary.wiley.com/doi/book/10.1002/9781444302677
SOIL_THERMAL_DIFFUSIVITY_M2_S | Soil thermal diffusivity [m2/s] [derivation: 1.6 (thermal conductivity of wet clay) / (2.4 * 10^6) (volumetric heat capacity of wet clay)] | 6.7e-07 | Verified assumption | David Banks - An Introduction to Thermogeology: Ground Source Heating and Cooling (pp 35, Table 3.1) | https://onlinelibrary.wiley.com/doi/book/10.1002/9781444302677
SURFACE_TEMP_PEAK_DOY | Day-of-year of annual surface-temp peak [-] | 200 | Verified assumption | Met Office: UK climate extremes (19 July 2022) | https://www.metoffice.gov.uk/research/climate/maps-and-data/uk-climate-extremes
BRINE_OFFSET_C | Brine inlet temp offset below ground T [degC] | 6 | Verified assumption | David Banks - An Introduction to Thermogeology: Ground Source Heating and Cooling (pp 191, Section 8.4 Carrier fluid flow conditions - Seasonal-average entering brine ~4-5 degC vs undisturbed ground ~10 degC => ~6 degC offset) | https://onlinelibrary.wiley.com/doi/book/10.1002/9781444302677
DEFAULT_GROUND_TEMP_C | UK undisturbed ground temp at borehole depth [degC]. Brine inlet = this minus BRINE_OFFSET_C. | 10 | Verified assumption | David Banks - An Introduction to Thermogeology: Ground Source Heating and Cooling (pp 42-49, Section 3.3 The temperature of the ground) | https://onlinelibrary.wiley.com/doi/book/10.1002/9781444302677
HORIZONTAL_COLLECTOR_M2_PER_KWTH | Horizontal slinky collector land area per kW_th of ground-loop capacity [m2/kW_th] | 25 | Verified assumption | Development of a Calculation Concept for Mapping Specific Heat Extraction for Very Shallow Geothermal Systems - (pp 9, Table 1; Trench Collector (Loam and Silt), x = 3,500 (Germany's HDD22/14)) | https://www.mdpi.com/2071-1050/14/7/4199
SITE_PLOT_RATIO | Plot ratio = gross floorspace / site area [-], used as site_area = floor_area / plot_ratio | 0.6 | Verified assumption | GLA London Employment Sites Database 2024 (published March 2026), (pp 7, Figure 4 plot ratio assumptions: 'Other' = 6,000 sq m/ha for both inner and outer London = 0.60 (1 ha = 10,000 m2). Outer London chosen as the closest analogue to the typical UK town where BEES-median stock sits.) | https://www.london.gov.uk/media/112350/download?attachment
PARKING_GROSS_M2_PER_SPACE | Gross land per car parking space incl. aisles and circulation [m2/space] | 25 | Standing assumption | A 2.4 x 4.8 m bay is 11.5 m2; doubled for aisle and circulation allowance.

## EV (DM)
Scope | Parameter | Description (units) | Value | Type | Source | Source URL
All | EV_CHARGER_KW | Installed charger rating [kW] - nameplate, per EV-enabled space. | 7 | Verified assumption | Office for Zero Emission Vehicles - Commercial chargepoints | https://www.gov.uk/guidance/commercial-chargepoints-minimum-technical-specification
All | EV_SPACE_FRACTION | Fraction of spaces EV-enabled [-] | 0.2 | Verified assumption | Building Regulations Approved Document S (2022): Requirement S4 and regulation 44G: New buildings other than residential or mixed-use buildings (pp 17, "cable routes for electric vehicle charge points must be installed in a minimum of one fifth of the total number of remaining parking spaces.") | https://assets.publishing.service.gov.uk/media/6218c5d38fa8f54911e22263/AD_S.pdf
Health: Hospital | EV_PARKING_DENSITY | Parking density [spaces/m2 GFA] [derivation: 1 / 50m2] | 0.02 | Standing assumption | - (no floor-area planning standard for hospitals; ~2 spaces/bed ÷ ~100 m² GIA per bed ≈ 1/50 m²)
Health: Hospital | EV_DWELL_HOURS | Representative dwell assumption [h] | 4 | Standing assumption | Assumption for clinical visit / staff shift

## Climate & Demand (DM)
Scope | Parameter | Description (units) | Value | Type | Source | Source URL
All | PEAK_FRACTION | Peak half-hour as fraction of annual demand [-] | 0.001 | Standing assumption | - (ESC modelling assumption: peak HH = 0.1% of annual)
All | T_SETBACK | Unoccupied setback temperature [degC] | 12 | Standing assumption | -
All | HDD_BASE | Heating degree-day base temperature [degC] | 15.5 | Verified assumption | UK standard HDD base | https://degreedays.net/
All | UK_LATITUDE | Representative latitude, England/Wales [deg N] | 52.5 | Standing assumption | - (representative for the solar-geometry model)
Summer | DIURNAL_AMPLITUDE | Diurnal temperature amplitude [degC] | 5.5 | Verified assumption | Half of peak-to-peak range, calculated from CIBSE Guide A Table 2.28 (pp 109-114) | https://ierga.com/wp-content/uploads/sites/2/2017/10/CIBSE-Guide-A-Environmental-design.pdf
Autumn | DIURNAL_AMPLITUDE | Diurnal temperature amplitude [degC] | 4 | Verified assumption | Half of peak-to-peak range, calculated from CIBSE Guide A Table 2.28 (pp 109-114) | https://ierga.com/wp-content/uploads/sites/2/2017/10/CIBSE-Guide-A-Environmental-design.pdf
Winter | DIURNAL_AMPLITUDE | Diurnal temperature amplitude [degC] | 3 | Verified assumption | Half of peak-to-peak range, calculated from CIBSE Guide A Table 2.28 (pp 109-114) | https://ierga.com/wp-content/uploads/sites/2/2017/10/CIBSE-Guide-A-Environmental-design.pdf
Peak Winter | DIURNAL_AMPLITUDE | Diurnal temperature amplitude [degC] | 2.5 | Verified assumption | Half of peak-to-peak range, calculated from CIBSE Guide A Table 2.28 (pp 109-114) | https://ierga.com/wp-content/uploads/sites/2/2017/10/CIBSE-Guide-A-Environmental-design.pdf
Spring | DIURNAL_AMPLITUDE | Diurnal temperature amplitude [degC] | 4 | Verified assumption | Half of peak-to-peak range, calculated from CIBSE Guide A Table 2.28 (pp 109-114) | https://ierga.com/wp-content/uploads/sites/2/2017/10/CIBSE-Guide-A-Environmental-design.pdf
Summer | SEASON_DOY | Representative mid-season day-of-year [-] | 172 | Standing assumption | - (21 June)
Autumn | SEASON_DOY | Representative mid-season day-of-year [-] | 274 | Standing assumption | - (1 October)
Winter | SEASON_DOY | Representative mid-season day-of-year [-] | 355 | Standing assumption | - (21 December)
Peak Winter | SEASON_DOY | Representative mid-season day-of-year [-] | 15 | Standing assumption | - (15 January)
Spring | SEASON_DOY | Representative mid-season day-of-year [-] | 80 | Standing assumption | - (21 March)
Health: Hospital | WE_LOAD_FACTOR | Weekend load factor [-] | 1 | Verified assumption | CIBSE TM46 Table 1, cat 20 (hospital, 7-day) (pp 4-9) | https://irp-cdn.multiscreensite.com/8c467baa/files/uploaded/CIBSE-TM46-Energy-Benchmarks.compressed.pdf